## Slide 1: Compliance Solutions for Health Based Issues
Techniques and Tools
Sterling L. Carroll, P.E., M.P.A.
FRWA State Engineer
Florida Rural Water Assn
Notes: In this presentation we will discuss the mechanism that produce disinfection by products, how to control their formation by the production of chloramines and how to prevent Nitrification as an unintended consequence of chloramination.

## Slide 2: Most Important Factor in providing Excellent Water Quality
The Operator
  Professional Attention & Care
  Proactive (not reactive)
    Look for problems
    Flushing
  Preventive Maintenance
    Calendared
    List actions that need to be taken
    Budget time and materials

## Slide 3: Source Water Quality Factors
Evaluate your source water first
  VOCs, SOCs, Inorganics
  Iron (Fe)
  Hydrogen Sulfide (H2S),
  Organics (TOC),
  TDS,
  Hardness (CaCO3),
  etc.

## Slide 4: Water Quality Factors
Treatment type & efficiency
  Is it effectively removing impurities?
  Chlorine feed
Distribution system conditions
  Age, pipe material, diameter, dead-ends…
  Biofilm, tuberculation, etc.
Homeowner’s piping

## Slide 5: Compliance Solutions Techniques and Tools
Oxidation by Aeration
Chemical Preoxidation
  Hydrogen Peroxide (H2O2)
  Permanganate (KMnO₄, NaMnO₄)
Absorption
  Activated Alumina Filtration
  GAC Filters
Ion / Anion Exchange
Reverse Osmosis

## Slide 6: Sources of Naturally Occurring Organic Material in Surface Water
Rain Events wash organic matter into receiving body - surface water
  Hydrophilic
  Dissolved organic matter
  Water can pass thru soil into Ground Waters
Algae Blooms are an example of organic material that is suspended or insoluble in water, hydrophobic
  Particulates easily removed by treatment
Notes: Natural Organic Matter makes up the humic content in source waters. NOM is either hydrophilic (more soluble in water) or hydrophobic (less soluble and a more aromatic fraction.) Hydrophobic matter is easier to remove in the treatment process.

## Slide 7: Naturally Occurring Organic Material
Hydro-PHILIC NOM
Attracted to water
Dissolved organic matter
Lighter molecular weight
Not easily removed by treatment
Not as reactive
Hydro-PHOBIC NOM
Insoluble in water
Suspended in water
Heavier molecular weight
  Long chain tannins
Particulates easily removed by treatment
Creates more TTHMs
Notes: Natural Organic Matter makes up the humic content in source waters. NOM is either hydrophilic (more soluble in water) or hydrophobic (less soluble and a more aromatic fraction.) Hydrophobic matter is easier to remove in the treatment process.

## Slide 8: Total Organic Content & Florida’s Groundwater
10
1.0
3
5
50
0.1
0.5
100
500
1,000
Sea Water
Surface Waters
WWTP Effluent
Wastewaters
Swamps
Florida Groundwater
Surface Water Median = 3.5 mg/L
Most Groundwaters
TOC (mg/L)

## Slide 9: Dissolved Organic Materials Examples
TEA
COFFEE

## Slide 10: Map of TDS Groundwater Quality relationship w/ TOC, Fe, H2S, etc.

## Slide 11: EPA Drinking Water Treatability Database https://oaspub.epa.gov/tdb/pages/general/home.do

## Slide 12
12

## Slide 13: Chloramines (The Last Choice Option)
A chlorine burn is considered “normal operations” & part of periodic maintenance
DBP Formation
Water line breaks are considered non-normal operating condition
Length of chlorine burns max. 21 days

## Slide 14: FDEP Memorandum May 10, 2018
To: DEP District and Approved County Health Department Offices
From: Source and Drinking Water Program
Subject: Clarification of Rule 62-550.822 Disinfection Byproducts (DBP) Requirements: Total Trihalomethanes (TTHM) and Haloacetic Acids (HAA5)

## Slide 15: FDEP Memorandum May 10, 2018
Scheduling Requirements for Quarterly Monitoring (62-550.822, F.A.C.)
For systems that monitor quarterly, regulatory offices must review DBP monitoring plans to identify the specific week of the quarter that will be sampled. For systems on annual monitoring, schedules must designate the specific month that will be sampled.

## Slide 16: FDEP Memorandum May 10, 2018
Clarification:
62-550.822 F.A.C adopted 40 CFR 141, Subpart U (Section 141.600-141.605) and 40 CFR 141, Subpart V (Section 141.620-141.629).
As stated in Subpart V in 40 CFR 141.621(a)(2) Footnote 2, Subpart U in §141.605(b) Footnote 2 and §141.605(e), systems on quarterly monitoring must sample every 90 days.
The 90-day rule was developed to allow an equal amount of time between sampling…

## Slide 17: FDEP Memorandum May 10, 2018
c. Samples used for compliance purposes must be designated in the system's State approved monitoring plan. Systems may collect more than the required number and frequency of sampling. However, in order to be used in the calculation of the quarterly average used for compliance purposes, the additional samples must be included in the monitoring plan and approved prior to collecting samples. Consideration should be given to assuring that the sampling is equally separated.

## Slide 18: FDEP Memorandum May 10, 2018
d. The definition of “normal operating conditions” include any routine maintenance practices. An event such as a chlorine burn, a switch from chloramine to chlorine, is considered to be part of the normal operations of a system for periodic maintenance. A water line break or other disruptive event which is outside the control of the facility is considered non-normal operating condition.

## Slide 19: FDEP Memorandum May 10, 2018
e. The length of chlorine burns should be kept to a maximum of 21 days. Whenever possible, systems should try to optimize processes using guidance such as AWWA manual “A Guide for the Implementation and Use of Chloramines” (2004).

## Slide 20: Chloramines NH2Cl (FRWA recommends against using ammonia)
Ammonia is a Waste By-product
  Ammonia does not improve water quality!
NH2Cl By-Products
  may be ultimately more health adverse
  future EPA regulation
Simultaneous Compliance & Water Quality Problems
  Nitrification - total loss of residual occurs w/o notice
  More flushing is needed – increased frequency & volume
  Do free chlorine burns deliver more DBPs than the MCL?
  Biofilm Regrowth
  Difficulty achieving CT 4-log compliance

## Slide 21: Oxidation by Aeration
Tank Aeration / Mixing
Aeration Techniques
Cascade Trays
Forced Draft Towers
Bubble Diffusers
Spray or
Air Induction
Notes: This is most common effective oxidation method

## Slide 22: Tank Aerators & Mixers
Port St Joe
Commercial ventilation fan
Small submersible pump
1¼” PVC piping
8 household showerheads
50 - 60 ppb 2nd Quarter
100 ppb 3rd Quarter
After DYI Aeration
20-40 ppb 4th Quarter
68% Decrease across all monitoring locations
< $7,500 ~ Port St Joe DYI solution
$25,000 to $35,000 Commercial Mixers

## Slide 23: Commercial Tank Mixers
GridBee GS-12 Submersible Mixer
PAX Water Technology

## Slide 24: Spray Aerators
Inexpensive
Less effective
More effective

## Slide 25: Spray Aerators
Inexpensive
Less effective

## Slide 26: Cascade Tray Aerators
Splashing & cascading
Produces small water drops that fall through the air
Approx. 15% to 25% total sulfide removal
Enhanced with H2O2
  H2O 18 g/mol
  H2O2 34 g/mol
Notes: Should be screened - #24 mesh

## Slide 27: Cascade Aerator w/ Packing
Packing increases the surface to air ratio  increases the gas exchange rate
More effective
Notes: Other aeration techniques include forced draft multiple trays, cascades. The cascade method shown directs water from tray to tray from top to bottom causing a high degree of exchange of oxygen with the water.

## Slide 28: Packed Tower Forced Draft Aerators
Forcing air up through column and packing as water falls
Most effective aeration
FDEP says > 90%
Notes: Packed towers are used to remove offensive odors such as hydrogen sulfide or Iron and Manganese from the water. Water is directed over synthetic media with large surface area to force contact of oxygen with water containing high concentrations of hydrogen sulfide. Removal efficiencies of 99% can be obtained with these systems.
Where high degrees of gas must be removed, a forced air system can be employed.
Following the aeration system a filtration system is employed to remove particulate iron, manganese and turbidity resulting from sulfur oxidation.

## Slide 29: Packed Tower Forced Draft Aerators
Notes: Packed towers are used to remove offensive odors such as hydrogen sulfide or Iron and Manganese from the water. Water is directed over synthetic media with large surface area to force contact of oxygen with water containing high concentrations of hydrogen sulfide. Removal efficiencies of 99% can be obtained with these systems.
Where high degrees of gas must be removed, a forced air system can be employed.
Following the aeration system a filtration system is employed to remove particulate iron, manganese and turbidity resulting from sulfur oxidation.

## Slide 30: Aerator Packing
Notes: Other aeration techniques include forced draft multiple trays, cascades. The cascade method shown directs water from tray to tray from top to bottom causing a high degree of exchange of oxygen with the water.

## Slide 31: Aerator Packing
Maintenance is REQUIRED!
Annual or Semiannual cleaning of aerator packing
Citric / Acetic Acid (potable)
Notes: Other aeration techniques include forced draft multiple trays, cascades. The cascade method shown directs water from tray to tray from top to bottom causing a high degree of exchange of oxygen with the water.

## Slide 32: Air Entrainment
From Pump
To Tank
Air Vent w/ down turned elbow
Install Screen on air line to protect against insects, frogs & debris
Air
Venturi Tee
But not before a hydropneumatic tank…

## Slide 33: Air Entrainment
Venturi Tee

## Slide 34: Chemical Preoxidation
Hydrogen Peroxide (H2O2)
Potassium Permanganate (KMnO4 solid granules) and Greensand Filtration
Sodium Permanganate (NaMnO4 solution) and Greensand Filtration

## Slide 35: Hydrogen Peroxide (H2O2)
Pharmacy Grade
3% Concentration
Same safety protocols as 12.5% NaOCl
55 gallon drum & Stenner pump
Industrial Grade
35% Concentration
Feed Rate ~ 3 mg/L
3% solution = 30,000 mg/L

## Slide 36: Jar Testing Hydrogen Peroxide
May 2012

## Slide 37: Hydrogen Peroxide (H2O2)
H2O2 is a Preoxidant
Chemically Oxidizes (Reduces) Impurities
  Iron, Sulfur, Organics, Tannins & TOC – all contribute to color, odor, and taste
Lowers chlorine demand = lowers DBPs
Installed Costs under $1,000
  easy to install
Treatment cost is about 5¢ / 1,000 gal treated
  Reduces chlorine usage by 50%

## Slide 38: Hydrogen Peroxide (H2O2)
Advantages
Controllable process
Inexpensive capital installation
Inexpensive chemical cost
Reduces ORGANIC color, odor & taste
Operation easy to understand & monitor
Long shelf life
  does not off gas
NO residuals
  only H2O & Oxygen
Disadvantages
Reaction / Contact Times 15-20 minutes
Incomplete oxidation
Dechlorinating agent
Does not reduce INORGANIC color, odor & taste
Must be jar tested
Turbidity – requires filtration
No direct sunlight

## Slide 39: Hydrogen Peroxide Vendors (H2O2)
Dave Symonds & Associates, Inc.
Leesburg FL 34788
800-226-0340
dsymonds@embarqmail.com
The Dumont Company, Inc.
Oviedo, Florida 32765
800-330-1369
ron.cartwright@dumontchemicals.com
Val-Co Marketing & Research
Quitman GA 31643
229-263-5120
Fax 207-729-6604
Hawkins Water Treatment Group
Thomasville, GA 31792
Cell: 850-712-3670
Russell.Burton@hawkinsinc.com

## Slide 40: Permanganate Pre-Oxidation
NaMnO4
Oxygen
Manganese
Sodium
KMnO4
Oxygen
Manganese
Potassium
Notes: The following four case study application of Sodium Permanganate were performed by FRWA. These studies demonstrate the benefit in using the chemical in selected applications. These application include the water systems at Fowlers Bluff, Otter Creek, Floral and Cross City. An additional application at Lake City was not included since high levels of H2S prohibited effective use of the chemical and the City has since started up a new water treatment facility.

## Slide 41: Permanganate Pre-Oxidation
Coagulation (10-15 min) and filtration required
Potassium Permanganate (KMnO4) used for decades in water treatment
Sodium Permanganate (NaMnO4) specific use because of higher cost
NaMnO4 is 15x more soluble than KMnO4, thus maintenance concerns are minimal

## Slide 42: Permanganate Pre-Oxidation
Permanganate do not create DBP’s
Strong oxidant / poor disinfectant
Difficult to overfeed since they are destroyed by chlorine oxidation
Good for TOC & Fe removal (poor H2S)

## Slide 43: Permanganate Pre-Oxidation

## Slide 44: Granular Activated Carbon Filters
EPA Best Available Technology for removal of DBP Precursors
Expected DBP Reduction 50% to 70%
Pilot Study Required
  Ten States Standards
  FDEP

## Slide 45
Most common adsorbent
Irregular particles, 0.2-5 mm dia.
  char of carbon material (wood or coal)
Activated exposure to steam at high temperature
  made more porous
1,000 m2 of adsorbing surface area per gram (~ 1 teaspoon)
  equivalent to 40 acre farm in one handful!
Granular Activated Carbon

## Slide 46
The Adsorption Process

## Slide 47
Adsorption:
the physical-chemical attraction of a solid material for a chemical in solution
In adsorption, the chemical being adsorbed is termed the ADSORBATE and the solid to which it sorbs is the ADSORBENT
Influent stream
The Adsorption Process

## Slide 48: PFAS ~ Per- and Polyfluoroalkyl Substances
GAC Media
Bench, pilot studies and full-scale applications, removals of up to greater than 99%
GAC can be quite effective for many PFAS compounds
  Perfluorobutanoic Acid (PFBA) 99%+ removal
  Perfluorobutyl Sulfonate (PFBS) 98%+ removal
  Perfluorohexyl Sulfonate (PFHxS) up to 98% removal
  Perfluorohexanoic Acid (PFHxA) up to 95% removal
  Perfluorononanoic Acid (PFNA) 93%+ removal
  Perfluorodecanoic Acid (PFDA) up to 97% removal

## Slide 49: PFAS ~ Per- and Polyfluoroalkyl Substances
Ion Exchange
Bench, pilot studies and full-scale applications, removals 57% to 99%
Effective for many PFAS compounds
  Perfluorobutanoic Acid (PFBA) 97%+ removal
  Perfluorobutyl Sulfonate (PFBS) 98%+ removal
  Perfluorohexyl Sulfonate (PFHxS) 99%+ removal
  Perfluorohexanoic Acid (PFHxA) 97%+ removal
  Perfluorononanoic Acid (PFNA) up to 98% removal
  Perfluorodecanoic Acid (PFDA) up to 98% removal

## Slide 50: Activated Alumina Filtration (Oxidation & Adsorption)
If nothing else works, this will…

## Slide 51: Activated Alumina Filtration (Adsorption)
Activated Alumina substrate
  Very hard & Durable
  Porous (exposed surface area >350m2/gm)
  Patented Chemistry - creates a new complex
  A strong oxidant
  High Adsorption capacity & Kinetics rate
  Effective over a wide pH range
  Contaminant metals bond permanently to media
Manufacturing Process
  Enables chemistry to penetrate Inner spaces of Activated Alumina to take full advantage of the surface area

## Slide 52: AP Oxidation Media
On-demand Oxidation & Adsorption Capability
  Very efficient Anti-Microbial capability
    Coliform, Iron & Sulfur Reducing Bacteria
  Arsenic III can be rapidly oxidized to Arsenic V
  Adsorption capability
Effective in any water
  industrial streams with high concentration of metals at varying oxidation states
No chlorine/dechlorination steps are required
  Removes annoying taste and odor.
  No generation of Disinfectant By Products (DBPs)

## Slide 53: AM Adsorption Media
Adsorption Only (no oxidation)
  Removes metals and semi-metals
    Arsenic,
    Fluoride,
    Iron &
    20 other metals and semi-metals
  Only Metals – No Hardness
  Creates a complex with media
  Metal contaminant will not leach out
  Spent media disposed in Landfill or Concrete Additive
  Very little pressure drop
    Fluoride,
    Selenium,
    Lead,

## Slide 54: AP Oxidation Field Test SR-6 / I-75 Hamilton County Water System, PWS: 2244150
Raw water is high in TDS, coliform hits, organics, etc.
  Tested Empty Bed Contact Times (EBCT )
    5 min. & and 10 min.
    Chlorine added: 4 drops NaOCl to a 16.9 oz bottle
Sample TOC HAA5 TTHM
(mg/L) (µg/L) (µg/L)
Raw well 5.5 - - - - - -
5 minute EBCT 1.4 0.52 0.14
10 minute EBCT 1.2 0.52 0.14
Chlorine added - - - 13.89 16.09

## Slide 55: AP Oxidation Field Test SR-6 / I-75 Hamilton County Water System, PWS: 2244150

## Slide 57: AP Oxidation Field Test SR-6 / I-75 Hamilton County Water System, PWS: 2244150
Current DBPs
Last 4 quarters TTHMs HAA5s
(µg/L) (µg/L)
21-Jun-17 57.8 55.3
27-Sep-17 531 792
5-Dec-17 300 231
14-Mar-18 704 546
LRAA 398.2 406.1

## Slide 58: AP Oxidation Field Test SR-6 / I-75 Hamilton County Water System, PWS: 2244150
74.5% of TOC was removed with 5 min. EBCT
76.4% of TOC was removed with 10 min. EBCT
99.87% of TTHM reduction with 5 or 10 min. EBCT
  398.2 to 0.52 µg/L
99.72% of HAA5 reduction with 5 or 10 min. EBCT
  406.1 to 1.14 µg/L

## Slide 59: Typical Adsorption Media Installation
Filter By-Pass Valve Normally Closed
Pressure Gauges both sides of all filters (typ. 4 places)
10-Micron Cartridge Filter
Duplex AP/AM Filters piped in Series
(no backwash)
Sample Tap with threads removed after all filters (typ. 4 places)
M
Potable Water to Distribution System
NaOCl

## Slide 61: AP Oxidation Costs
NSF Std. 60
Installed Costs about $3.65 / 1,000 gal treated
Treatment cost is about 53¢ / 1,000 gal treated
Much more effective than GAC
  More costly than GAC
Soon to be testing media life
  Hoping that it lasts 4 to 6 longer than GAC medias

## Slide 62: ElectroCoagulation Gerber Pumps International, Inc.
Passing electrical current through water, to attract salt ions on one plate and anions to another.
effective removal of contaminants

## Slide 63: ElectroCoagulation Gerber Pumps International, Inc.

## Slide 64: ElectroCoagulation Gerber Pumps International, Inc.

## Slide 65: ElectroCoagulation Gerber Pumps International, Inc.
1.5 gpm unit $8,500 / month
10 gpm unit $15,000 / month
Technician/Engineering Support @ $1,000 / day
O&M costs
Energy costs: 2-7 kwh/1000 gal processed
Blade replacement: $0.04 -0.08/1000 gal
Typically $0.20 - $0.50/1000 gal

## Slide 66: Reverse Osmosis ~ Nanofiltration
Suwannee W&S District Bids
RO Plant 375,000 gpd
Total Cost $4,165,035
$11.11 per gallon - 2004
$26.40 per gallon - 2021
Uses Wastewater Sprayfield

## Slide 67: Reverse Osmosis ~ Nanofiltration
St Johns Harbor Water Assn
Near Palatka 355 Population
RO Plant 130,000 gpd
Const Cost $2,000,000 ~ Bare Bones
  Bid Costs $2,900,000 ~ Removed Some Components from Design Plans
$15 per gallon - 2006
$31.80 per gallon - 2021
Percolation Ponds for Brine Disposal

## Slide 68: Reverse Osmosis ~ Nanofiltration
Town of Inglis
Firm RO Plant Capacity: 648,000 gpd
Const Cost $1,000,000 +/-
Completed 2000
NO Iron Pretreatment 2007 + $516,000
$2.34 per gallon
$6.30 per gallon – 2021
Very Low Bid = Osmonics trying to break into Potable Water Market
WWTP Sprayfield for Brine Disposal

## Slide 69: Reverse Osmosis ~ Nanofiltration
Preliminary Cost Estimates $20M to $32M
Most Expensive O&M of All Power & Chemicals
Sprayfield Disposal Costs $500,000+
Deep Well Disposal over $5 million

## Slide 70: Water Treatment Plant Construction Costs
Project Costs – $ per gal
Plant Capacity (MGD)
$25
$20
$15
$10
$5
$0
1
2
3
4
0
5
Category II
Category IV
Category III
Notes: Reaction continues to occur as long as:
  Residual Chlorine
  Organics Available to React

## Slide 71: Summary of Options to Improve Water Quality
Option | Application | Installation Costs | Treatment Costs
Automatic Flushing Valves | Reduce water age, DBPs & chlorine demand | $300 to 5,000 | None
Tank Aerators & Mixers | Turnover tank water, lower DBPs & chlorine demand | $7,500 to $35,000 | Minimal power
Air Entrainment via Venturi Tee | Increase aeration, lowers DBPs & chlorine demand | < $500 | None
Hydrogen Peroxide (H2O2) | Chemical oxidation, lowers DBPs & chlorine demand | < $1,000 | 5¢ / 1,000 gal
Chlorine Dioxide (ClO2) Applied Oxidation | Chemical oxidation, greatly reduces DBPs, lowers or completely replaces chlorine | $2,000 | 7 to 10¢ / 1,000 gal
Activated Alumina Adsorption / Oxidation Media | Chemical oxidation & media adsorption of impurities, greatly reduces DBPs & chlorine | $3.65 / 1,000 gal | 53¢ / 1,000 gal
Reverse Osmosis ~ Nanofiltration | Removal of particulate & microbial contaminants and large organic molecules | $25 to $32 / gal | 
71