### Effective Flushing Techniques for Water Systems

### Introduction

Most water systems experience problems with slow moving water or stagnant water in their water distribution systems. These problems can be customer complaints about taste and odor, corrosion problems that lead to build up of slime and chemical deposits in pipelines, loss of disinfection residual and growth of coliform bacteria, to list just a few. To minimize these types of problems most water systems resort to flushing.

Unfortunately, unless consideration is given to the methods used in the flushing program, flushing can actually cause additional problems and complaints and result in large quantities of lost water and ineffective use of limited personnel.

This paper examines methods that have been found to be effective in eliminating many problems caused by slow moving water and provides simple tools that can be used by water system operators to improve current flushing programs.

### Preventing Problems in Water Distribution Systems

To avoid problems in water distribution systems a water operator has three basic tasks: 1.) ensuring that water is turned over in the water distribution system’s pipelines to maintain disinfection residual, 2.) ensuring that sediment in dead-end lines is removed to minimize chlorine demand and buildup of regulated disinfection by-products and 3.) ensuring that water detention times in storage tanks is not causing loss of disinfection and causing pipeline problems when the water is released. Fortunately, all of these problems can be solved by a proper flushing program.

Figure 1

Correcting Water Storage Tank Problems

Recommended Turnover for Water Storage Tanks

Georgia: Daily Goal, 50% of

Storage Volume

Virginia: Complete Turnover

Every 72 hrs.

Ohio:       Daily Goal, 20% of

Storage Volume;

Recommended 25%

Finished Water Storage Facilities, USEPA, August 2002

### Where to Expect Problems in a Water Distribution Systems

Studies of water distribution systems have repeatedly shown that bacteriological hot spots are 3 to 4 times more likely to occur at dead end areas in a distribution system. Studies of water movement in water storage tanks also confirm the fact that water in tanks tends to stratify and does not mix.

Other studies have shown that most water systems have water detention times of 7 to 24 days and the smaller the water system, the more likely it is to have longer detention times. In essence all water systems will benefit from a well designed flushing program.

Components of a Well Designed Flushing Program

The components of a well designed flushing program include basic procedures that that operators can easily understand and implement. These are illustrated in the following table:

Table 1

Components of a Well Designed Flushing Program

| # | Description |
| --- | --- |
| 1. | Locate dead-end mains and low-use areas on a water distribution map |
| 2. | Locate all flush points such as fire hydrants and flush valves nearest to the affected areas |
| 3. | Label flush points in the field to aid in timely field identification |
| 4. | Schedule the flushing program in the hours of lowest flow and or when disinfection by-product formation is at the highest |
| 5. | Always notify the customers in the affected areas |
| 6. | Where flushing is directed at specific problems, place these areas on a monthly schedule |
| 7. | Place the rest of the hydrants and valves on less frequent flushing schedules |
| 8. | Make sure that water storage tanks are turning over by using a tank level recorder |

### Designing the Flushing Program

There are two types of flushing programs that have been successfully used by water system operators, and they are targeted on very specific problems. These are: traditional or conventional flushing and unidirectional flushing (UDF).

Figure 2

Differences Between Conventional

and Unidirectional Flushing

Conventional Flushing

< 2.5 fps velocity that reduces water age, raises disinfectant residual removes coloration

## Unidirectional Flushing

> 2.5 fps  velocity that removes solid deposits and biofilm from pipelines

Conventional Flushing

Flushing Procedures and Hydrant Maintenance,

# Texas Commission on Environmental Quality

Conventional flushing is directed at reducing water age, raising disinfection residuals and removing coloration caused by iron problems. In a conventional flushing program only one flushing point is generally used at one time and water velocity is held to below 2.5 feet per second. In general, conventional flushing is successful when about 3 pipelines of water volume is flushed from the main. The chart below may be used to estimate this volume:

A unidirectional flushing program is directed at removing solid deposits and biofilm from pipelines. Unidirectional flushing can often remove deposits and slime growth that exert chlorine demand and cause corrosion problems. Flushing is much less expensive than all other alternatives.

Table 2

#### Gallons of Water to Flush to Achieve

Three (3) Volumes of Pipeline

|  | # Feet of Pipeline |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Main Size dia” | 100 | 200 | 300 | 400 | 500 |
| 2 | 50 | 100 | 150 | 200 | 250 |
| 3 | 110 | 220 | 330 | 440 | 550 |
| 4 | 200 | 400 | 600 | 800 | 1000 |
| 6 | 440 | 880 | 1320 | 1600 | 2200 |

Determining Flow Velocities for Various Pipeline Sizes

Flow velocities for various pipeline sizes can be estimated for flushing purposes within reasonable accuracy in the field, without the use of meters or pitot tubes.

Flow from a fire hydrant can be approximated by attaching a pressure gauge to the 2 ½ inch nozzle and flowing from the other nozzle. The table below will provide reasonable accuracy when using this method.

Table 3

Estimating Flow from a 2 1/2 “ Fire Hydrant Nozzle

with a Pressure Gauge on Opposite Nozzle in GPM

| Pressure at Gauge | Approx. FH Flow | Pressure at Gauge | # Approx. FH Flow |
| --- | --- | --- | --- |
| 1 | 170 | 11 | 555 |
| 2 | 240 | 12 | 580 |
| 3 | 290 | 13 | 605 |
| 4 | 340 | 14 | 630 |
| 5 | 380 | 15 | 650 |
| 6 | 410 | 16 | 670 |
| 7 | 440 | 17 | 690 |
| 8 | 480 | 18 | 710 |
| 9 | 500 | 19 | 730 |
| 10 | 530 | 20 | 750 |

To obtain smaller flows or for estimating flows from a 2” blow off the following table may be used. For conventional flushing do not exceed 3 feet per second to avoid stirring up deposits that can enter customer residences. When flushing, always alert customers to avoid using water and not to do laundry on the day that flushing is being performed. This will keep sediment from entering residences. Generally door hangers and personal notification is effective to avoid these types of customer complaints.

Table 4

Estimating Flow from Blow Off Valves and Fire Hydrants

### for Flow Ranges Below 150 GPM in GPM

| ## X | Flow 2” | Flow 2 ½ ” |
| --- | --- | --- |
| 6 | 21 | 30 |
| 8 | 28 | 40 |
| 10 | 35 | 50 |
| 12 | 42 | 60 |
| 14 | 49 | 70 |
| 16 | 56 | 80 |
| 18 | 63 | 90 |
| 20 | 70 | 100 |
| 30 | 77 | 150 |

Hydraulic Handbook, Colt Industries

Determining How Long to Flush and How Many GPM are Needed to Achieve Desired Results

The above methods can be used to determine the flow rate from blow off valves or fire hydrants in gallons per minute (GPM) using simple field procedures. Now all that is left to do is to determine how long to flush to achieve the desired result. Flushing too long will waste valuable water and flushing at too high a rate will move sediment and rust and make problems worse. The following tables can be used together to estimate how long to flush to achieve the desired results.

Table 5

Determining the Flow Velocity 	   Determining How Long to Flush

Using Estimated GPM above             in minutes for Flow Velocity Estimated

| Length; 100’; 200’; 300’; 400’; 500’. Flush Vel.; Time for 3 Volumes of Pipeline (min.). 3 fps; 1:40; 3:20; 5:00; 6:40; 8:20. 4fps; 1:15; 2:30; 3:45; 5:00; 6:15. 5fps; 1:00; 2:00; 3:00; 4:00; 5:00. | # Velocity in Pipeline |  |
| --- | --- | --- |
| Size of Main dia | 3 fps | 5fps |
| 2 | 30 | 50 |
| 4 | 120 | 200 |
| 6 | 260 | 450 |
| 8 | 470 | 775 |
| 12 | 1,060 | 1,750 |
| 16 | 7,500 | 12,500 |

### Conclusion

The methods described above can greatly enhance the water distribution system operator’s success in achieving flushing goals. When combined with a good public notification program the flushing program can achieve the desired goals while achieving improved customer satisfaction and improved water quality.

References:

- Finished Water Storage Facilities, USEPA, August 2002

- Flushing Procedures and Fire Hydrant Maintenance, Texas Commission on Environmental Quality, September 2006

- Hydraulic Handbook, Colt Industries, Ninth Edition, 1975