O & M Manual

and

Preventative Maintenance Logs

For Drinking Water Systems

Per Chapter 62-555.350 (2); (12) & (13) F.A.C.

O&M Manual and Preventive Maintenance Logs

Water System:

Street Address:

City, State, Zip:

Phone: 	 Fax:

Contact:

E-mail:

Number Connections:

PWS:

County:

Classification:  Community 	 Non-Community 	 NTNC

Source:  Ground 	 Surface 	 Purchased

Ownership:

Date:

R

U

R

A

L

R

T

W

A

E

R

O

L

A

D

I

F

A

I

S

O

A

S

C

T

I

O

N

R

F

W

A

For more information or additional copies of this document contact:

### FLORIDA RURAL WATER ASSOCIATION

2970 Wellington Circle ~ Suite 101 ~ Tallahassee FL 32309

Telephone: 850-668-2746 ~ Fax: 850-893-4581

e-mail: FRWA@frwa.net

### Table of Contents

Section  	Section Description	Page

Preface	 DEP Requirements 	3

Operation & Maintenance Manual

Preventative Maintenance Log

Section 1 	 Maintenance Contacts List	4

Service / Repair Contacts

Section 2 	 Bound & Indexed Equipment Manufacturer Manuals	5

System Description & Major Equipment

Source or Sources of Water (Wells)

Types of Treatment

Major Controls

Storage & Distribution Features

Section 3 	 Preventative Maintenance Log	6

Recommended Daily Preventative Maintenance

Recommended Weekly Preventative Maintenance

Recommended Monthly Preventative Maintenance

Preventative Maintenance Recommendations

Suggested Preventative Maintenance Logs

Appendix A	 Emergency Response Plan *	16

Appendix B 	 Permits & Specific Conditions * 	17

Appendix C 	 System Description & Reports *	18

Appendix D 	 General System Operation & Control *	19

Appendix E 	 Laboratory Testing *	20

Appendix F 	 Storeroom & Inventory System *	21

Appendix G 	 Emergency / Safety Program *	22

* NOTE: This information in Appendices A thru G is RECOMMENDED by FRWA for inclusion with your O&M Manual and Preventative Maintenance Logs, but is not specifically required by FDEP in Rule 62-555.350 (2), (12) and (13) FAC.

DEP Requirements

O&M Manual and Preventative Maintenance Logs

This template has been developed to help you prepare your own O&M Manual and Preventive Maintenance Log.

OPERATION & MAINTENANCE MANUALS

Manual

O&M

Who: 	ALL water systems regardless of size

What: 	Up-To-Date Operation & Maintenance Manual of Your System

When: 	December 31, 2005

Where:	Keep a copy in your water plant office

Why: 	Rule 62-555.350(13), FAC

The O&M Manual should be a quick reference for successful daily operation and include anything from trouble shooting to emergency procedures. The rule requires the O&M Manual to contain:

- Bound and Indexed Equipment Manufacturer Manuals (you can download most of these manuals off of the web or get them from equipment manufacturers)

- Operation and Control Procedures

- Preventive Maintenance and Repair Procedures

Preventative

Logs

Maintenance

We recommend that you make at least two copies of the O&M Manual and store one in a safe place in case the plant copy gets lost or damaged by normal use. Your O&M Manual and Preventive Maintenance Logs can be stored in a 3-ring binder.

PREVENTIVE MAINTENANCE LOGS

Who: 	ALL water systems regardless of size

What: 	Up-To-Date Preventive Maintenance Logs of Your System

When: 	August 28, 2003

Where:	Keep a copy in your water plant office

Why: 	62-555.350 (2) and 62-555.350 (12), FAC

We recommend that you include the Preventive Maintenance Logs in your O&M Manual Binder. The Preventive Maintenance Logs show the date and type of all maintenance performed, and complies with rule 62-555.350 (2) and 62-555.350 (12), which requires the following:

- Preventive Maintenance Logs on Electrical and Mechanical Equipment

- Cleaning and Inspection Logs of Treatment Facilities and Storage Tanks

- Records of Coatings and Linings Rehabilitation or Repair

- Licensed Engineer Inspection Report (once every 5-years) for Finished-Drinking-Water Storage Tanks and Hydropneumatic Tanks

- Written Flushing Program and Logs showing that Dead-End Water Mains are being flushed at least quarterly

- Isolation Valves Exercise Logs

However upon completion, DO NOT submit your O&M Manual & Preventative Maintenance Logs to the Florida Department of Environmental Protection  (FDEP). FDEP will verify that you have these documents during their Sanitary Survey of your system (routine water system inspection). This template is intended for use by small water systems and may be modified to fit the specific needs of each system. This O&M Manual & Preventative Maintenance Logs complies with FDEP minimum requirements and; you may modify it in any way that works for you – add sections, or rearrange them if you wish. Please send a copy of your O&M Manual & Preventative Maintenance Logs to Florida Rural Water Association ~ we would like to see your work!

### Section 1 – Maintenance Contacts List

This Operations & Maintenance (O&M) Manual is to used as a reference in the overall operation and maintenance of this Water System. This manual contains the necessary O&M procedures, worksheets, and record keeping forms, safety and emergency procedures, and testing and monitoring procedures. This manual is to be updated from time to time to reflect physical and procedural changes to the water system. Also it is intended that this manual be used as a training tool for new employees and as a guide for qualified substitute operators.

State Warning Point Duty Officer Telephone: 800-320-0519 62-555.350(10)(a) Suppliers of water shall telephone the SWP immediately (i.e., within two hours) after discovery of any actual or suspected sabotage or security breach, or any suspicious incident, involving a public water system.

| Service / Repair Contacts |  |  |  |  |
| --- | --- | --- | --- | --- |
| Organization or Company | Name & Position | Telephone | Cell Phone | e-mail |
| Water Testing Lab |  |  |  |  |
| Water Testing Lab |  |  |  |  |
| Pump Supplier |  |  |  |  |
| Equipment Vendor |  |  |  |  |
| Equipment Vendor |  |  |  |  |
| Equipment Vendor |  |  |  |  |
| Rental Equip |  |  |  |  |
| Chemical Supplier |  |  |  |  |
| Chlorine Supplier |  |  |  |  |
| Electrical Contractors |  |  |  |  |
| Safe Dig / One Call |  |  |  |  |
| Excavating Contractors |  |  |  |  |
| Eng. Consultants |  |  |  |  |

### Section 2 - Bound and Indexed Equipment Manufacturer Manuals

Attach ALL Equipment Manufacturer Manuals in this Section.

System Description & Major Equipment (Attach additional sheets if needed)

Source or Sources of Water (Wells, FL Unique ID #)

Well Pumps (Size, Mfr & Model)

Types of Treatment (e.g., Chlorination, Filtration, etc.)

Chlorine Feed Equipment (Size, Mfr & Model)

Ammonia Feed Equipment (Size, Mfr & Model)

Ortho/Polyphosphate Feed Pumps (Size, Mfr & Model)

Other Chemical Feed Equipment (Size, Mfr & Model)

Treatment Equipment (Size, Mfr & Model)

Treatment Equipment (Size, Mfr & Model)

Treatment Equipment (Size, Mfr & Model)

Standby Power Equipment (Size, Mfr & Model)

Major Controls

Control Valves (Size, Mfr & Model)

Pump Controls (Type, Mfr & Model)

Other Controls (Type, Mfr & Model)

Storage & Distribution Features

High Service Pumps (Size, Mfr & Model)

High Service Pumps (Size, Mfr & Model)

High Service Pumps (Size, Mfr & Model)

Storage Tanks (Size, Mfr & Model)

Storage Tanks (Size, Mfr & Model)

Storage Tanks (Size, Mfr & Model)

We suggest attaching a water treatment plant schematic and system map / diagram to show system components, including sampling taps (POC's or points of collection) which are used for bacteriological and chemical sampling, also see recommended Appendices for optional O&M information.

### Section 3 - Preventative Maintenance Log

It is essential that water system operators provide Preventative Maintenance for protection of the health and safety of the public; proper equipment operation and preservation; and as required by the Florida Department of Environmental Protection. Your water system may be more complex, if so you will need to add additional Preventive Maintenance categories.

The purpose of any maintenance program is: to ensure that equipment is properly functioning, to maximize system reliability, to ensure that equipment meets or exceeds its expected service life and to ensure that equipment repairs can be performed in a scheduled manner avoiding the extra costs and disruptions caused by unexpected equipment failure.

There are three kinds of maintenance activities that you will perform. These are predictive, preventative and breakdown maintenance. Predictive Maintenance includes such items as oil analysis, to determine optimal oil replacement frequency, infrared analysis, to ensure that electrical connections are sound and that there are no imminent electric failures about to occur and vibration analysis, to ensure that equipment is properly aligned and that bearing wear is identified well before failure occurs.

Preventive Maintenance is a schedule of planned maintenance actions aimed at the prevention of breakdowns and failures in water systems. The primary goal of preventive maintenance is to prevent the failure of pumps and equipment before it actually occurs. It is designed to preserve and enhance equipment reliability by replacing worn components before they actually fail. Preventive maintenance activities include exercising valves and fire hydrants; equipment and tank inspections; partial or complete overhauls at regular specified periods; oil changes; lubrication; and so on. In addition, operators can record equipment deterioration so they know to replace or repair worn parts before they cause system failure.

How often should preventive maintenance for equipment be performed?

- Once every week

- After a breakdown

- According to manufacturer recommendations

- When time permits

- According to a well thought out plan

The answer is both C and E. The ideal preventive maintenance program would prevent all water system equipment failure before it occurs. Long-term benefits of preventive maintenance include: improved system reliability, decreased cost of replacement, decreased system downtime, and better spares inventory management.

Breakdown Maintenance is maintenance that must be performed because of unexpected equipment failure. This is the most disruptive and costly type of maintenance and the purpose of a good maintenance program is to minimize these unscheduled events. There are multiple misconceptions about the benefits of preventive maintenance. One such misconception is that preventive maintenance is unduly costly, time consuming, or causes disproportionate work. This logic dictates that it would cost more for regularly scheduled downtime and maintenance than it would normally cost to operate equipment until failure or repair is absolutely necessary. This may be true for some smaller equipment components; however, one should compare not only the costs but also the long-term benefits and savings associated with preventive maintenance. Without a sound preventive maintenance program, labor costs for lost water production time from unscheduled equipment breakdown will be incurred, damages to equipment can be much more severe and potential negative treatment process and/or regulatory ramifications can be unacceptable to the customer and costly to the system.

Even under the best preventative maintenance program, some breakdown maintenance will occur. Each of these events provides a learning opportunity to improve upon existing preventative maintenance programs. The operator should evaluate every equipment breakdown situation, to determine the cause, and what measures could have been taken to prevent the occurrence. The lessons learned should then be added to the preventative maintenance program. Building these written feedback loops into the preventative maintenance program will yield significant returns.

Other Maintenance Items ~ FRWA has provided a number of recommended charts that can be very helpful in designing or in improving an existing preventative maintenance system, Water Systems are advised to use these to develop customized maintenance information documentation for operators and maintenance personnel that are specific to their systems. General maintenance is imperative in keeping a plant in working condition. The following items should be included;

- Preventative maintenance schedule and instructions for completion;

- List of Specifications for fuels, lubricants, filters, etc. for equipment;

- Trouble shooting charts or guides which references pages in O&M manual and manufactures O&M manual;

- Record system for each type of equipment, this should include; numbering system, catalog, nameplate data cards, maintenance record cards;

- Manufacturers’ maintenance schedule for routine adjustments. A summary with references to page number in manufacturer’s O&M manual needs to be provided;

- A work order system for maintenance of equipment with sample forms.

- A designated responsible individual to ensure that the program tasks are being met and that timely updates are included in the program as needed

- Lastly, another benefit of a sound preventative maintenance program is the ability to identify maintenance trends that consume a great deal of the operator’s time. In these cases these trends provide the documentation necessary to management for replacement of equipment that is not performing in an acceptable manner. A preventative maintenance program that is used in this way can achieve significant cost reductions, improve system reliability, and provide the operator with more time to devote to more critical tasks.

###### TYPICAL DUTIES OF A WATER PLANT OPERATOR

- Start up, shut down, and make periodic operating checks of plant equipment, such as pumping systems, chemical feeders, auxiliary equipment (compressors), and measuring and control systems.

- Perform routine preventative maintenance, such as lubrication, operating adjustments, cleaning and painting equipment.

- Load and unload chemicals, such as chlorine cylinders, bulk liquids, powdered chemicals, and bagged chemicals either by hand or using chemical –handling equipment such as forklifts and hoists.

- Perform minor corrective maintenance on plant mechanical equipment; for example, chemical feed pumps and small units.

- Maintain plant records, including operating logs, daily diaries, chemical inventories, and data logs.

- Monitor the status of plant operating guidelines, such as flows, pressures, chemical feeds, levels, and water quality indicators, by reference to measuring systems.

- Collect representative samples and perform laboratory tests on samples for turbidity, color, odor, coliforms, chlorine residual, and other tests as required.

- Order chemicals, repair parts and use tools.

- Estimate and justify budget needs for equipment and supplies.

- Conduct safety inspections, follow safety rules for plant operations, and also develop and conduct tailgate safety meetings.

- Discuss water quality with the public, conduct tours of your plant (especially for school children), and participate in your employer’s public relations program.

- Communicate effectively with other operators and supervisors on the technical level expected for your position.

- Make arithmetic calculations to determine chemical feed rates, flow quantities, detention and contact times, and hydraulic loadings as required for plant operations.

Recommended Daily Operational Duties / Preventative Maintenance

(check or circle items that apply ~ strikethrough items that do NOT apply)

| Water Meter Readings | - Record Water Plant Meter Readings - Calculate Total Daily Production |
| --- | --- |
| Pumps & Tank Levels | - Inspect Well Pumps & Controls - Check Chemical Solution Tanks & Record Amount Used - Check & Record Water Levels in Storage Tanks - Inspect Chemical Feed Pumps - Inspect High Service Pumps & Controls - Record Pump Run Times & Start Cycles |
| Sampling & Readings | - Check & Record Chlorine Residual at Point of Application - Check & Record Chlorine Residual at Nearest Customer (Systems Req’d to Provide CT) - Check & Record Chlorine Residual in Distribution System at Remote Points - Check Instrumentation for Proper Input / Output |
| Security | - Investigate Customer Complaints - Complete a Daily Security Check - Windows, Doors, Hatches, Vents, Screens for Evidence of Tampering or Vandalism - Well Caps, Vents & Seals - Security Lighting, Locks & Alarms - Inspect Fences & Gates |

Recommended Weekly Operational Duties / Preventative Maintenance

(check / circle items that apply ~ strikethrough items that do NOT apply)

| Inspections & Conditions | - Inspect Chlorine & Fluoride Testing Equipment (Calibration & Reagents) - Check & Record Well Pumps Pumping Rate - Check Membrane System Pressure Differential |
| --- | --- |
| Cleaning | - Clean Pump House and/or Plant Operations Office - Clean Water System Grounds |
| Security | - Check ALL Station Alarms for Proper Operation - Check Stand-By Power Source to Ensure Emergency Operation |

Recommended Monthly Operational Duties / Preventative Maintenance

(check or circle items that apply ~ strikethrough items that do NOT apply)

| Inspections & Conditions | - Check & Record Electric Meters - Take Appropriate Monthly Water Quality Samples - Check & Record Static & Draw-Down (Pumping) Levels in Wells - Confirm Submittal of Monthly Operation Reports (MORs) - Lubricate Pumps, Motors, Blowers & ALL Moving/Rotating Equipment - Inspect ALL Pumps House Water Lines, Gaskets & Fittings for Corrosion & Leaks - Inspect Pump, Seals, Water Lines & Fittings for Corrosion & Leaks - Listen to Pump for Unusual Noises (or signs that Bearings are Wearing Out) - Inspect Scales, Analyzer / Alarm, Oxygen Breathing Apparatus, Cross Ventilation - Inspect Filter Head for Leaks - Inspect and Add Salt to Brine Tank (i.e. Ion Exchange Only) - Run Emergency Generator for 30-min UNDER LOAD, Check ALL Fluid and Fuel Levels - Test Eye Wash & Emergency Shower |
| --- | --- |
| Cleaning | - Clean & Inspect Wellheads - Inspect & Clean Chlorine Injection Points |
| Security | - Inspect Tank Overflow Vent Screens, Ensure Screen Intact, Check Manway Hatch & Ensure it is Secured |

Recommended Quarterly Operational Duties / Preventative Maintenance

(check or circle items that apply ~ strikethrough items that do NOT apply)

| Cleaning | - Flush Dead-End Lines (Feb, May, Aug & Nov) Required by FDEP Rule 62-555.350(2) or more often per your written flushing program * - Lubricate Locks - Clean, Inspect & Disinfect Aerator / Degassifier Screens, Sprayheads & Gaskets |
| --- | --- |

* Note: Flushing of dead-end water mains may be limited to just those dead-end mains that are 6 inches or greater in diameter if there is no history of water quality problems at dead-end mains smaller than 6 inches in diameter.

Preventative Maintenance (PM) Recommendations

January PM Recommendations (Peak Month)

(check or circle items that apply ~ strikethrough items that do NOT apply)

- Flush Half Distribution System - Exercise Half Fire Hydrants

February PM Recommendations (Peak Month)

(check or circle items that apply ~ strikethrough items that do NOT apply)

- Flush Remaining Distribution System & Exercise Remaining Fire Hydrants (not completed in January) - Flush Dead-End Lines (Feb, May, Aug & Nov) Required by FDEP Rule 62-555.350(2) or more often - Inspect, Clean & Repair Control Panels in Water Treatment Plant

March PM Recommendations (Peak Month)

(check or circle items that apply ~ strikethrough items that do NOT apply)

- Inspect Storage Tanks for Defects & Sanitary Deficiencies - Clean Storage Tanks as Needed - Structural Inspection of Tank & Coatings by Engineer at Least Every 5-yrs and Before Aug 2008 (Clean Tank Prior) - Perform Tank Coating Repairs per Mfr Specifications & Recommendations - Clean, Inspect & Disinfect Aerator / Degassifier Screens, Sprayheads & Gaskets

April PM Recommendations

(check or circle items that apply ~ strikethrough items that do NOT apply)

- Clean & Inspect Chemical Feed Lines - Clean & Inspect Chemical Solution Tank - Calibrate Chemical Feed Pumps

May PM Recommendations (Non-Peak Month)

(check or circle items that apply ~ strikethrough items that do NOT apply)

- Flush Distribution System - Exercise ALL Fire Hydrants & Check FH Valves - Water Plant & Pump House Building Preventive Maintenance - Flush Dead-End Lines (Feb, May, Aug & Nov) Required by FDEP Rule 62-555.350(2) or more often

June PM Recommendations

(check or circle items that apply ~ strikethrough items that do NOT apply)

- Contact Electrician to Check Emergency Generator & Run on Load Bank - Contact Electrician to Check Running Amps on Pumps - Make Sure Unnecessary Equipment is Properly Decommissioned - Review Emergency Response Plan – Update as Necessary - Clean, Inspect & Disinfect Aerator / Degassifier Screens, Sprayheads & Gaskets

July PM Recommendations (Non-Peak Month)

(check or circle items that apply ~ strikethrough items that do NOT apply)

- Prepare Water System for Summer Operation / Hurricane Season (Fuel, Generators, Shutters) - Building Preventive Maintenance

August PM Recommendations (Non-Peak Month)

(check or circle items that apply ~ strikethrough items that do NOT apply)

- Operate ALL Valves Inside Treatment Plant & Pump House - Clean & Inspect ALL Safety Equipment - Flush Dead-End Lines (Feb, May, Aug & Nov) Required by FDEP Rule 62-555.350(2) or more often

September PM Recommendations

(check or circle items that apply ~ strikethrough items that do NOT apply)

- Clean RO Membranes or per Mfr Recommendations - Overhaul or Replace Pressure Relief Valves on Hydropneumatic Tanks – every 5-yrs or per Mfr Recommendations - Test Pressure Reducing Valves & RPZs - Clean, Inspect & Disinfect Aerator / Degassifier Screens, Sprayheads & Gaskets

October PM Recommendations

(check or circle items that apply ~ strikethrough items that do NOT apply)

- Overhaul Chemical Feed Pumps (Feeder Head Cleaned, O-Rings, Check Valves & Diaphragms, Worn-Out Parts Replaced) - Clean & Inspect Chemical Feed Lines - Clean & Inspect Chemical Solution Tanks - Calibrate Chemical Feed Pumps after Overhaul - Test Eye Wash & Emergency Shower

November PM Recommendations

(check or circle items that apply ~ strikethrough items that do NOT apply)

- Exercise HALF of ALL Mainline Valves (You may consider combining Valve Exercising with your Flushing & FH Exercising Program if this is appropriate for your system) - Check Water Meter For Accuracy (2" or Less Every 3-yrs Recommended) or Annually per Mfr Recommendations - Change Media in Filter or per Mfr Recommendations - Flush Dead-End Lines (Feb, May, Aug & Nov) Required by FDEP Rule 62-555.350(2) or more often

December PM Recommendations (Peak Month)

(check or circle items that apply ~ strikethrough items that do NOT apply)

- Exercise Remaining HALF of ALL Mainline Valves (not exercised in November) - ALL Safety Equipment - Clean & Inspect - Clean, Inspect & Disinfect Aerator / Degassifier Screens, Sprayheads & Gaskets - Clean, Inspect & Disinfect Aerator / Degassifier

### Suggested Preventative Maintenance Log

Your water system may be more complex, if so you will need to add categories. (Strikethrough items that do NOT apply)

| ###### Category | Suggested Frequency | Last Service (Date) | Service (Date) | Service (Date) | Service (Date) |
| --- | --- | --- | --- | --- | --- |
| ###### Well / Source Water |  |  |  |  |  |
| Clean & Inspect Wellheads, Pump, Controls Seals, Vent & Screen | Monthly |  |  |  |  |
| Check & Record Static & Draw-Down (Pumping) Levels in Wells | Monthly |  |  |  |  |
| ###### Water Plant & Pump House |  |  |  |  |  |
| Inspect Water Lines, Gaskets & Fittings for Corrosion & Leaks | Monthly |  |  |  |  |
| Lubricate Pumps, Motors, Blowers and ALL Moving / Rotating Equipment | Monthly |  |  |  |  |
| Building Preventive Maintenance | Annually - July |  |  |  |  |
| Exercise ALL Valves Inside Treatment Plant & Pump House (AWWA M44 once 2-yrs) | Annually - Aug |  |  |  |  |
| Check Water Meter For Accuracy (2" or Less Every 3-yrs Recommended) | Every 4-yrs - Nov (or per Mfr) |  |  |  |  |
| ###### High Service Pumps |  |  |  |  |  |
| Inspect Pump, Seals, Water Lines & Fittings for Corrosion & Leaks | Monthly |  |  |  |  |
| Listen to Pump for Unusual Noises (or signs that Bearings are Wearing Out) | Monthly |  |  |  |  |
| ###### Safety & Security |  |  |  |  |  |
| ALL Safety Equipment - Clean & Inspect (Lock Out Tags) | Annually - Dec |  |  |  |  |
| Emergency Response Plan Review/Update | Annually - June |  |  |  |  |
| ###### Chemical Feed Systems (Liquid) |  |  |  |  |  |
| Inspect Pump, Seals, Water Lines & Fittings for Corrosion & Leaks | Monthly |  |  |  |  |
| Clean Chlorine Injection Points | Monthly |  |  |  |  |
| Overhaul Chemical Feed Pumps (Feeder Head Cleaned, O-Rings, Check Valves & Diaphragms, Worn-Out Parts Replaced) | Annually - Oct |  |  |  |  |
| Test Eye Wash & Emergency Shower | Bi-annually Apr & Oct |  |  |  |  |
| Chemical Feed Lines - Clean & Inspect | Bi-annually Apr & Oct |  |  |  |  |
| Chemical Solution Tanks - Clean & Inspect | Bi-annually Apr & Oct |  |  |  |  |
| Calibrate Chemical Feed Pumps | Bi-annually Apr & Oct |  |  |  |  |
| ###### Chemical Feed Systems (Gas) |  |  |  |  |  |
| Inspect Scales, Analyzer / Alarm, Oxygen Breathing Apparatus, Cross Ventilation | Monthly |  |  |  |  |
| Inspect & Clean Chlorine Injection Points | Monthly |  |  |  |  |

### Suggested Preventative Maintenance Log (continued)

Your water system may be more complex, if so you will need to add categories. (Strikethrough items that do NOT apply)

| ###### Category | Suggested Frequency | Last Service (Date) | Service (Date) | Service (Date) | Service (Date) |
| --- | --- | --- | --- | --- | --- |
| ###### Aerator / Degassifer |  |  |  |  |  |
| Inspect Screens, Sprayheads & Gasket | Annually - Dec |  |  |  |  |
| Clean, Inspect & Disinfect Aerator / Degassifer | Annually - Dec |  |  |  |  |
| ###### Filter / Water Softener |  |  |  |  |  |
| Inspect Filter Head for Leaks | Monthly |  |  |  |  |
| Inspect and Add Salt to Brine Tank (i.e. Ion Exchange Only) | Monthly |  |  |  |  |
| Change Media in Filter | Per Mfr - Nov |  |  |  |  |
| Reverse Osmosis / Membrane Softening Unit |  |  |  |  |  |
| Check Pressure Differential | Weekly |  |  |  |  |
| Clean Membranes | Annually – Sep or per Mfr |  |  |  |  |
| Replace Membranes | per Mfr |  |  |  |  |
| Storage Tanks – attach Inspection Reports with preventative maintenance plan |  |  |  |  |  |
| Inspect Overflow Vent Screens, Ensure Screen Intact, Check Manway Hatch & Ensure it is Secured | Monthly |  |  |  |  |
| Inspect Storage Tanks for Defects, Leaks & Sanitary Deficiencies | Annually - Mar |  |  |  |  |
| Clean Storage Tanks if Needed | Annually – Mar |  |  |  |  |
| Structural Inspection of Tank & Coatings by Engineer (Clean Prior to Inspection) | Every 5-yrs - Mar (Before Aug 2008) |  |  |  |  |
| Perform Coating Repairs per Mfr Specs | Annually - Mar |  |  |  |  |
| Replace Pressure Relief Valves on Hydropneumatic Tanks | Every 5-yrs - Sep (or per Mfr) |  |  |  |  |
| ###### Controls, Electrical & Stand-By Power |  |  |  |  |  |
| Inspect, Clean & Repair Control Panels in Water Treatment Plant | Annually - Feb |  |  |  |  |
| Prepare Water System for Summer Operation / Hurricane Season | Annually - July |  |  |  |  |
| Run Emerg Generator 30-min under load | Monthly |  |  |  |  |
| Contact Electrician to Check Emergency Generator & Run on Load Bank | Annually - Jun |  |  |  |  |
| Contact Electrician to Check Running Amps on Pumps | Annually - Jun |  |  |  |  |
| Distribution System (You may consider combining Exercising and Flushing Programs if this is appropriate for your system) * |  |  |  |  |  |
| ###### Exercise ALL Mainline Valves | Annually Jan & Feb | See Chart | on Next | Page |  |
| Flush Distribution System & Exercise ALL Fire Hydrants | Annually Nov & Dec | See Chart | on Next | Page |  |
| ###### Flush Dead-End Lines | Quarterly - Feb, May, Aug & Nov |  |  |  |  |

Flushing of dead-end water mains may be limited to just those dead-end mains that are 6 inches or greater in diameter if there is no history of water quality problems at dead-end mains smaller than 6 inches in diameter.

### Suggested Preventative Maintenance Log (continued)

Exercise ALL Mainline Valves - Annually Jan & Feb (add sheets as needed)

| ###### Valve ID # | Valve Location | Last Service (Date) | Service (Date) | Service (Date) | Service (Date | Service (Date) |
| --- | --- | --- | --- | --- | --- | --- |

### Suggested Preventative Maintenance Log (continued)

Exercise ALL Fire Hydrants - Annually Nov & Dec (add sheets as needed)

| ###### FH ID # | Fire Hydrant Location | Last Service (Date) | Service (Date) | Service (Date) | Service (Date | Service (Date) |
| --- | --- | --- | --- | --- | --- | --- |

### Suggested Preventative Maintenance Log (continued)

Flush Distribution System - Annually Nov & Dec (add sheets as needed)

Flush Dead-End Lines (Feb, May, Aug & Nov) Required by FDEP Rule 62-555.350(2) or more often per your written flushing program.

| ###### Pipe ID # | Pipe Segment Location | Last Service (Date) | Service (Date) | Service (Date) | Service (Date | Service (Date) |
| --- | --- | --- | --- | --- | --- | --- |

| EXAMPLE VALVE RECORD |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Location (street / address): |  |  |  |  |  |  |
| Type: |  |  |  | Make: | Size: |  |
| Opens:  Left  Right  Other: |  |  |  |  | # of Turns: |  |
| Date Installed: |  |  |  |  |  |  |
| Date Exercised | Closes/Opens? (Y / N) | # of Turns | Condition of Stem, Packing, Nut, Gearing, Etc. |  |  | Valve Status (Open or Closed) |

| EXAMPLE DEAD-END WATER MAIN FLUSHING RECORD |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Location (street): |  |  |  |  |  |
| Flushing Date | Flushing Duration (min.) | Water Characteristics (color, odor, etc.) |  | Disinfectant Residual, mg/L |  |
|  |  | Before Flushing | After Flushing | Before Flushing | After Flushing |

### Appendix A – Emergency Response Plan

This information in Appendices A thru G is RECOMMENDED by FRWA for inclusion with your O&M Manual and Preventative Maintenance Logs, but is not specifically required by FDEP in Rule 62-555.350 (2), (12) and (13) FAC.

Insert your ERP here.

How FRWA can help: We encourage you to use the Florida Rural Water Association’s Emergency Response Plan (ERP) templates and guides off our website. You can easily download these on-line at www.frwa.net - just click on “security” and download any of the ERP documents. We are ready to help you complete your ERP. Please call your Water Circuit Rider or the FRWA Engineer for assistance.

### Appendix B – Permits & Specific Conditions

This information in Appendices A thru G is RECOMMENDED by FRWA for inclusion with your O&M Manual and Preventative Maintenance Logs, but is not specifically required by FDEP in Rule 62-555.350 (2), (12) and (13) FAC.

Insert PERMITS and SPECIFIC CONDITIONS for your Water System here. Include any FDEP or DOH provisions for your water system plus any applicable rules, regulations, latest Sanitary Survey, and Water Management District Consumptive Use Permit.

Boil Water Notices

Health advisories usually take the form of a drinking water warning or boil water advisory.  Communication during these times is critical.  DEP / DOH staff are committed to working closely with water systems to determine if an advisory is needed.  Health advisories should always be well thought out and provide very clear messages.

Use the assistance of your County Health Department and/or District DEP office, located on DEP’s website at: http://www.doh.state.fl.us/environment/water/manual/boil.htm

TYPES OF BOIL WATER NOTICE INCIDENTS

    - Microbiological Contamination

    - Zero or Negative Pressure.

    - Low Water Pressures

    - Water Main Breaks/Interruptions.

    - Flooding of Wells.

ATTACHMENT A

(DATE)

PRECAUTIONARY BOIL WATER NOTICE

TO:	RESIDENTS OF (NAME OF CITY, TOWN, TRAILER PARK, SUBDIVISION OR COUNTY) LIVING IN THE AREA BOUNDED BY (STREET, AVENUE, CANAL OR OTHER DESCRIPTIVE BOUNDARY)

(BRIEF DESCRIPTION OF EVENT SUCH AS: BACTERIOLOGICAL ANALYSES OF SAMPLES OBTAINED FROM YOUR WATER DISTRIBUTION SYSTEM HAVE SHOWN POSSIBLE CONTAMINATION OF THE WATER, OR A WATER MAIN BREAK HAS OCCURRED AT _________________, OR A LOSS OF WATER PRESSURE HAS BEEN EXPERIENCED DUE TO _____________________)

THEREFORE, AS A PRECAUTION, WE ADVISE THAT ALL WATER USED FOR DRINKING OR COOKING BE BOILED.  A ROLLING BOIL OF ONE MINUTE IS SUFFICIENT.  AS AN ALTERNATIVE BOTTLED WATER MAY BE USED.

THIS "PRECAUTIONARY BOIL WATER NOTICE" WILL REMAIN IN EFFECT UNTIL THE PROBLEM HAS BEEN CORRECTED AND A BACTERIOLOGICAL SURVEY SHOWS THAT THE WATER IS SAFE TO DRINK.

IF YOU HAVE ANY QUESTIONS YOU MAY CONTACT (NAME OF PERSON, AGENCY) AT (PHONE NUMBER).

(                SIGNATURE                )

(NAME, TITLE AND AGENCY OF

OFFICIAL ISSUING THE NOTICE)

Boil Water Notices (continued)

ATTACHMENT B

(DATE)

RESCISSION OF PRECAUTIONARY BOIL WATER NOTICE

TO:	RESIDENTS OF (NAME OF CITY, TOWN, TRAILER PARK, SUBDIVISION OR COUNTY) LIVING IN THE AREA BOUNDED BY (STREET, AVENUE, CANAL OR OTHER DESCRIPTIVE BOUNDARY)

THE (DATE) "PRECAUTIONARY BOIL WATER NOTICE" IS HEREBY RESCINDED FOLLOWING THE (ACTION TAKEN TO CORRECT THE PROBLEM) AND THE SATISFACTORY COMPLETION OF THE BACTERIOLOGICAL SURVEY SHOWING THAT THE WATER IS SAFE TO DRINK.

IF YOU HAVE ANY QUESTIONS, PLEASE CALL (NAME, AGENCY) AT (PHONE NUMBER).

(               SIGNATURE               )

(NAME, TITLE AND AGENCY OF

OFFICIAL RESCINDING THE NOTICE)

### Appendix C – System Description & Reports

This information in Appendices A thru G is RECOMMENDED by FRWA for inclusion with your O&M Manual and Preventative Maintenance Logs, but is not specifically required by FDEP in Rule 62-555.350 (2), (12) and (13) FAC.

A General System Description should include:

- Description of Treatment Processes

- Principal Design Criteria and Process Equipment Ratings

- Water System Map indicating Major Valves and Water Storage Tanks

- Process Flow Schematic Water Treatment System

- Brief Description of Interconnections

- Mutual Aid Agreements with Adjacent Water Systems / FlaWARN

Records and Reports. Keeping and compiling records is a valuable part of an efficient water system. The following should be included in the manual:

- A general explanation of the importance of records & reports;

- The system should maintain a list of complaints and identify responses made;

- Daily logs, maintenance records, laboratory records, monthly reports, monitoring reports, annual reports, operating cost reports, accident reports, and sanitary surveys. Examples and sample reports of each should be included;

- A listing of records that are on file (permits and standards, consumption);

- Location of records on file;

- Procedures for reporting records to appropriate agencies;

- Specify how long records should be kept on file;

Water Treatment Plant As-Builts, Equipment Manuals and Vendor Catalogues. Maintaining a current set of plant drawings, equipment manuals and vendor catalogues is critical in promoting timely repairs and reduces the chances for accidental equipment damage. The following should be provided:

- As-Builts of all Plant piping and valving and a method for updating the information

- A centralized storage area that is accessible by those needing the information should be made available in the plant.

- Plant equipment manuals should be maintained in a visible and accessible location

- Current vendor supply catalogues

How FRWA can help: We are ready to help you complete your O&M Manual, please call your Water Circuit Rider or the FRWA Engineer for assistance.

### Appendix D – General System Operation & Control

This information in Appendices A thru G is RECOMMENDED by FRWA for inclusion with your O&M Manual and Preventative Maintenance Logs, but is not specifically required by FDEP in Rule 62-555.350 (2), (12) and (13) FAC.

A general System Operation and Control. It is important to fully understand how the water system operates. This section should include;

- Identification of Major System Components including a description of the normal operation of the component. Show the relationship of each component with other system components, and relate any possible alternative operation modes and circumstances under which they would be used. Include schematic diagrams of each unit and discuss any special features that may be of importance.

- Preventative Maintenance Program; describe for each major component the preventative maintenance tasks (if any) that are performed. This should include types of preventative maintenance or inspection required; frequency of maintenance or inspection; and any extraordinary changes to operations which would occur when a facility is off-line.

- Common Operating Problems should be discussed along with methods of bypassing units, and the importance of and how to use laboratory tests for unit control.

- Routine System Operation; for each major system component describe the routine operational tasks that are performed and controlled. This should include start-up and shut down procedures, safety procedures, meter reading and how system performance is evaluated.

- Special Task Lists. These lists should identify assignments to personnel for notifying regulatory agencies, the media, institutional customers such as hospitals, government buildings or schools and special needs customers who require a continuous supply of water. The list should also include who is authorized as a spokesperson to represent the water system.

- Staff Contact and Capability Lists. This should include a list staff, emergency contact and listing of any training or ability to perform specialized tasks such as electrical work, welding, operation of CDL vehicles or construction equipment, test equipment, or specialized knowledge in maintenance or operational activities through training, licensing or experience.

How FRWA can help: We are ready to help you complete your O&M Manual, please call your Water Circuit Rider or the FRWA Engineer for assistance.

### Appendix E – Laboratory Testing

This information in Appendices A thru G is RECOMMENDED by FRWA for inclusion with your O&M Manual and Preventative Maintenance Logs, but is not specifically required by FDEP in Rule 62-555.350 (2), (12) and (13) FAC.

A general Laboratory Testing. This should include any samples and tests needed for compliance as well as for process control. For samples taken by the State, or taken by the system and analyzed by a State laboratory:

- Type of sample

- Sampling locations;

- Monitoring schedule;

For tests to be performed by outside laboratories:

- Name of the laboratory

- Contact person

- Telephone number

- Type of sample

- Sampling locations;

- Monitoring schedule;

### Appendix F – Storeroom & Inventory System

This information in Appendices A thru G is RECOMMENDED by FRWA for inclusion with your O&M Manual and Preventative Maintenance Logs, but is not specifically required by FDEP in Rule 62-555.350 (2), (12) and (13) FAC.

Having the proper equipment, tools, parts and consumable supplies is critical in maintaining the treatment process and plant equipment operation. Equipment owned by the system should be maintained in good working order and should be available to the employees who may need it for use at all times. Similarly, stocks of spare parts, special tools, supplies, chemicals, and other consumable items should be maintained in a secure storage location with controlled access. An inventory tracking and reorder system that identifies  who has used the equipment and consumable parts must be maintained so that acceptable levels of inventory are available when needed and restocked to facilitate timely actions. Minimum FRWA recommendations for managing plant inventory are listed below:

- Plant Property, Rolling Stock (vehicles, tractors, construction equipment and trailers), and Assigned Equipment and Furniture

- An inventory of all property and equipment, both moveable and non-moveable, owned by the system;

- A mechanism for assigning specific items of moveable equipment to individual employees (e.g. vehicles, tools, etc.)

- A mechanism for tracking specific items of moveable equipment by location (e.g. furniture, office equipment, etc.)

- A mechanism for storage and checking out of specialized items of equipment needed infrequently.

- Brief operation instructions for each item of equipment with reference to the manufacturers’ technical specifications for major system components;

- List of warranted equipment and the warranty provisions;

- List of outside contract maintenance tasks;

- List of equipment manufacturers and local suppliers;

- Spare Parts and Specialized Tools list;

- Special tools list and tools displayed prominently

- Spare Parts Inventory, number available and reorder quantity

- Lists of special test equipment and operating manuals

- List of major suppliers with telephone numbers and contact persons;

- A system of requisitions and/or work orders used to distribute parts, supplies, chemicals, etc. to employees.

- Lists of equipment and spare parts should clearly indicate those items of equipment and parts that are essential to the operation of the system.

- List, number and types of valves, reducers, pipe and repair fittings that are on-hand;

- Hand Tools, raingear, and miscellaneous hardware used in the plant

Chemicals and Other Consumable Items

- Recommended stock levels of supplies and chemicals and method of reordering when stock on hand drops below recommended levels;

- Delivery dates and critical chemicals such as chlorine, lime, polymers, etc

- Laboratory Supplies and reorder quantities (generally maintained by the Lab)

- Identification of responsible party for maintaining of critical inventories

- List of major suppliers with telephone numbers and contact persons

### Appendix G – Emergency / Safety Program

This information in Appendices A thru G is RECOMMENDED by FRWA for inclusion with your O&M Manual and Preventative Maintenance Logs, but is not specifically required by FDEP in Rule 62-555.350 (2), (12) and (13) FAC.

Emergency / Safety Program

- An Operating Plan For Emergencies and the procedures to be followed until normal operation can be resumed. This plan should include personnel assignments, emergency equipment inventory, and emergency numbers. Phone numbers to keep readily accessible should be police and fire departments, and for chemical spills or exposure CHEMTECH 800 424-9300. The emergency call up list should identify, in ranked order, water system personnel responsible for making decisions in specific situations. This list should include the job title, home and work phone number (beeper/car phone number if available) for all personnel.

- A Contingency Plan should also be made to insure proper treatment of water even inadverse conditions. This plan should describe conditions and procedures for putting standby and emergency sources into active service. Procedures for notifying customers, the local health jurisdiction, and DEP of noticeable water quality problems. Sample Public Notices should be prepared for acute Tier I violations and water borne disease outbreaks that must be distributed within 24-hours.

- Safety Procedures should identify work space hazards for the waste water system. Potential hazards include asbestos coated pipes, mechanical equipment, electrical, explosion and fire, chlorine, oxygen deficiency, laboratory and any chemicals used by the plant. A potential danger at plants can stem from the chlorination process. The manual should provide information on how to do the following tasks;

1. Handling of Chlorine Containers.

- Forklift trucks or hoisting equipment with special cradles or carriages designed for chlorine equipment are used for lifting cylinders;

- Proper storage of containers;

- Tag empty containers, and store separate from full cylinders;

- Use cylinders in order that they are received;

- Use ONLY approved tools;

- Cylinder emergency repair kits should be readily available;

2. Emergency Procedures and Emergency Equipment.

- Written procedures in event of catastrophic leak or container rupture.

- Self-contained pressure helmets; with own compressed air supply and full-face piece; located at readily accessible points, away from area(s) likely to be contaminated with chlorine gas.

- Spare cylinders on site for use during prolonged emergencies.

- Inspect helmets, emergency kits, and breathing air supply tanks routinely.

- Formal training with drills for potential users of helmets and emergency equipment.

3. Leak Detection

- A strong solution of aqueous ammonia is available for use in locating source of leaks

- Repairs of chlorine leaks are to be done by at least two people. Protecting gear should be used, and if below grade, safety harnesses and ropes are worn and emergency rescue operators are present.

- Piping and valves in chlorine rooms should be color coded and labeled for rapid identification.

- Properly train repair people.

How FRWA can help: We are ready to help you complete your O&M Manual, please call your Water Circuit Rider or the FRWA Engineer for assistance.