CROSS-CONNECTION CONTROL MANUAL

As compiled by the

Florida Rural Water Association

2970 Wellington Circle W, Suite 101

Tallahassee FL 32309

Phone:  850-668-2746 Fax:  850-893-4581

Revised  November, 2006

Includes DEP/TREEO Comments

Table of Contents

Chapter 1    Introduction to Cross-Connection Control	4

Who is required to have a Cross-Connection Control Program?	4

What is the purpose of a Cross-Connection Control Program (CCC)?	4

What is a Cross-Connection Control Program?	4

What is a Cross-connection?	4

What is backflow?	4

What is backpressure?	4

What is back siphonage?	5

Why do water suppliers need to control backflow?	5

What should water suppliers do to protect their water systems against backflow?	5

What backflow assemblies are acceptable to DEP?	5

Why do backflow preventers have to be tested periodically?	6

Establishing and Implementing a Written Cross-Connection Programs	7

DEP Minimum Requirements for a Written Cross-Connection Control Program	7

Backflow Protection Provided in a Written Cross-Connection Control Program	7

Examples of Customers that have Potential to Cause Health Problems	7

Health Hazards that the Water Purveyor must Address	8

Definitions of Health Hazards	8

Acceptable Backflow Prevention Assemblies for Health Hazards	8

Backflow Prevention Assemblies Application for Health and Low Health Hazards	9

Backflow Device and Health Hazard Appliations	9

Consideration for Fire Service Lines	9

Considerations for Backflow Containment	10

Backflow Isolation and Considerations for Use	11

Chapter 2     Selection and Installation of Approved Backflow Prevention Assemblies	12

Air Gap (AG)	13

Double Check Valve Assembly (DCVA)	15

Residential Dual Check Valve	16

Pressure Vacuum Breaker (PVB)	17

Atmospheric Vacuum Breaker (APV)	18

Hose Bibb Vacuum Breaker (Isolation)	19

Chapter 3     Establishing an Approved DEP Cross-Connection Control Program	20

Step 1 – Legal Authority and Development of Cross-Connection Control Policy	20

Requirements for Legal Authority for CWS	20

Cross-Connection Control Program Policy Requirements	20

Step 2 - Policy Requirement for Backflow Preventers for Health Hazards	20

Cross-Connection Control Backflow Prevention Requirements	21

Step 3 -  Policy for Standards Materials and Installation of Backflow Preventers	21

Standards for Backflow Prevention Assemblies and Methods of Installation	21

Step 4 -  Policy for Testing and Maintenance of Backflow Preventers	22

Policy for the Testing and Maintenance of Backflow Prevention Assemblies	22

Schedule for Field Testing and Maintenance of Backflow Assemblies	22

Minimum Qualifications for Backflow Prevention Field Testers	22

Step 5 -  Procedures for Assessing New & Existing Service Connections for BFP’s	23

Procedures for Assessing New and Existing Service Connections	23

Requirements for Testing by type of Backflow Assemblies:	24

Step 6 – Establish a Procedure for Keeping Cross-Connection Control Records	24

Essential Policy for a Cross-Connection Control Program 	25

Type and Format of Records to be Maintained	25

Records Retention Requirements	25

Step 7 – Procedures for Enhanced Public Education and Inspection Enhancement	26

Public Education Policy and Procedures for Cross-Connection Control	26

FAC 62.555.360 - Cross-Connection Control for Muncipal Public Systems	27

Model Cross-Connection Policy for Non-Municipal Community Water Systems 	28

Frequently Asked Questions	32

Appendix 1 – Notification to Customer   Inspection of Connections	44

Appendix  2 – Notification to Customer of Cross-Connection Violation	45

Appendix  3 – Cross-Connection Survey Form  Commercial & Industrial Facilities	46

Appendix  4 – Backflow Prevention Assembly  Test and Maintenance Form	47

Appendix  5-  Customer Notice  Requirements for Backflow Prevention Inspection	48

Appendix  6 – Customer Notice Requirements for Backflow Replacement	49

Appendix  7 - FRWA Cross-Connection Control Program – Model Ordinance	50

Appendix  8 - Cross-Connection Educational Brochure for Homeowners	50

Appendix  9 – Standard Color Coding for - Water Works Facilities…………………59

Acknowledgements

This document was prepared with the assistance of the Florida Department of Environmental Protection, various Approved County Health Departments and the University of Florida TREEO Center.

The policies and procedures presented here represent Best Management Practices. However, it is highly advisable to consult local DEP Districts or Approved County Health Departments when questions arise and all those engaged in Cross Connection Control Programs should receive training through the University of Florida TREEO Center in Gainesville Fl.

Introduction to Cross-Connection Control

#### Who is required to have a Cross-Connection Control Program?

Community water systems, shall establish and implement a routine cross-connection control program to detect and control cross-connections and prevent backflow of contaminants into the water system.

#### What is the purpose of a Cross-Connection Control Program (CCC)?

The purpose of any Cross-Connection Program is to protect the public water system (PWS) from contamination or pollution via backflow due to backpressure or backsiponage.

#### What is a Cross-Connection Control Program?

A Cross-Connection Control Program is a written plan that is developed using recommended practices of the American Water Works Association set forth in Recommended Practice for Backflow Prevention and Cross-Connection Control, AWWA Manual M14.

#### What is a cross-connection?

A cross-connection is any temporary or permanent connection between a public water system or consumer’s potable (i.e., drinking) water system and any source or system containing nonpotable water or other substances. An example is the piping between a public water system or consumer’s potable water system and an auxiliary water system, cooling system, well, or irrigation system.

#### What is backflow?

Backflow is the undesirable reversal of flow of nonpotable water or other substances through a cross-connection and into the piping of a public water system or consumer’s potable water system. There are two types of backflow; backpressure and backsiphonage.

#### What is backpressure ?

Backpressure is backflow caused by a downstream pressure that is greater than the upstream or supply pressure in a public water system or consumer’s potable water system. Backpressure (i.e., downstream pressure that is greater than the potable water supply pressure) can result from an increase in downstream pressure, a reduction in the potable water supply pressure, or a combination of both. Increases in downstream pressure can be created by pumps, temperature increases in boilers, etc. Reductions in potable water supply pressure occur whenever the amount of water being used exceeds the amount of water being supplied, such as during water line flushing, fire fighting, or breaks in water mains.

#### What is backsiphonage?

Backsiphonage is backflow caused by a negative pressure (i.e., a vacuum or partial vacuum) in a public water system or consumer’s potable water system. The effect is similar to drinking water through a straw. Backsiphonage can occur when there is a stoppage of water supply due to nearby fire fighting, a break in a water main, or any other situation that causes a significant loss in water system pressure..

#### Why do water suppliers need to control backflow?

Backflow into a public water system can pollute or contaminate the water in that system (i.e., backflow into a public water system can make the water in that system unusable or unsafe to drink), and each water supplier has a responsibility to provide water that is usable and safe to drink under all foreseeable circumstances. Furthermore, consumers generally have absolute faith that water delivered to them through a public water system is always safe to drink. For these reasons, each water supplier must take reasonable precautions to protect its public water system against backflow.

#### What should water suppliers do to protect their water systems against backflow?

Water suppliers that are required by DEP to implement Cross-Connection Control Programs must ensure that a proper backflow preventer is installed and maintained at the water service connection to each system or premises that poses a hazard or a potential health threat to the public water system. This would include the water service connection to each dedicated fire protection system, to each in-ground irrigation piping system, water service connections to premises with an auxiliary or reclaimed water system service and commercial, industrial and institutional facilities that may pose a health threat to the public water supply system. Each water supplier must also ensure that a DEP specified backflow preventer is installed and maintained at each water service connection noted above.

#### What backflow assemblies are acceptable to DEP?

Backflow assemblies that are acceptable to DEP for protection of the water supply system at the service connection are:

(a) Air gap separation

(b) Reduced pressure principle backflow prevention assembly.

(c) Atmospheric vacuum breaker

(d) Pressure vacuum breaker assembly.

(e) Double check valve assembly.

(f) Residential Dual Check (testable and non-testable)

What backflow protection assembly should be used?

Backflow protection assemblies are installed on the basis of an existing or a potential introduction of contaminants or pollutants into the water supply system. The specific requirement for a backflow assembly is made on the basis of the existing or potential health hazard.

The best means of preventing backflow is an air gap, which either eliminates a cross-connection or provides a barrier to backflow. However, air gaps are many time not feasible and mechanical backflow prevention assemblies are used.

The basic mechanism for preventing backflow and backsiponage is the reduced-pressure principle assembly. Other assemblies and devices such as a pressure vacuum breaker or an atmospheric breaker may be appropriate when no backpressure condition exists and only backsiphonage is a concern. Where only backpressure and low hazard is a concern a double check valve assembly is appropriate.  A secondary type of mechanical backflow preventer is the residential dual check valve that is approved for very limited applications where customers are in areas that are served by reclaimed water but have no other hazards on their property.

#### Why do backflow preventers have to be tested periodically?

Mechanical backflow preventers have internal seals, springs, and moving parts that are subject to fouling, wear, or fatigue. Also, mechanical backflow preventers and air gaps can be bypassed. Therefore, all backflow preventers have to be tested periodically to ensure that they are functioning properly. A visual check of air gaps is sufficient, but mechanical backflow preventers have to be tested with properly calibrated gauges and other specialized  equipment.

Inspection of backflow assemblies must be performed by a certified backflow prevention assembly tester.

Considerations in the Development of a Cross-Connection Program

#### Establishing and Implementing a Written Cross-Connection Programs

A Cross-Connection program is required for any Community Water Systems (CWS)  and in service areas also served by reclaimed water. CWS shall establish and implement written Cross-Connection Control programs using recommended practices of AWWA manual M-14 .

#### DEP Minimum Requirements for a Written Cross-Connection Control Program

A written Cross-Connection program must include at least the following seven (7) components:

- Legal Authority

- Policy establishing the requirements for the appropriate backflow preventor at service connections constituting a hazard to a CWS.

- Policy regarding the material and installation standards for backflow preventors at service connections

- Policy regarding the testing and maintenance of Backflow preventors at service connections.

- Procedures for assessing new or existing service connections to determine need for Backflow preventors.

- Procedures for keeping CCC records of assemblies, devices and testers.

- Procedures for enhanced public education & enhanced inspections (required if using/allowing Dual Check Valves at service connections to residential premises served by reclaimed water

#### Backflow Protection Provided in a Written Cross-Connection Control Program

A written cross-connection control program must protect the CWS water mains from contamination from external sources. It does not generally protect users within the customer's facility(s). CWS water mains are generally protected by containing any existing or potential contamination to the customer’s side of the water meter.

#### Examples of Customers that have Potential to Cause Health Problems

Facilities with a backflow potential include residential, commercial or industrial facilities where:

1.) there is an auxiliary water supply which is connected to the potable

water piping; or,

2.) there is piping for conveying liquids other than potable water, where that

piping is under pressure and is installed in proximity to potable water

piping; or,

3.) there is intricate plumbing which makes it impractical to ascertain

whether or not cross-connections exist; or,

4.) there are cross-connections or potential cross-connections.

#### Health Hazards that the Water Purveyor must Address

The water purveyor is responsible for protecting the community water supply system form any actual or potential backflow hazards. The degree of hazard is the potential risk to health and the potential adverse effects upon the public water supply based on the probability of backflow occurring and the type or nature of the contaminant.

#### Definitions of Health Hazards

A health hazard or high hazard is any condition, device or practice which creates or may create a danger to the health and well being of the water consumer. The degree of hazard is related to the toxicity of the substance or its virulence if microbes are present that may backflow, and the possibility that a backflow could occur.

AWWA’s M14, defines two categories of health hazards. These are shown below:

Health Hazards as Described by AWWA

Recommended Practices for Backflow Prevention

And Cross-connection Control M14

| Contaminant Classification | Description |
| --- | --- |
| Health or High Hazard (Contaminant) | A cross-connection or potential cross-connection involving any substance that could, if introduced into the potable water supply, cause death, illness, spread disease, or have a high probability of causing such effects. |
| Non-health or Low Hazard (Pollutant): | A cross-connection or potential cross-connection involving any substance that generally would not be a health hazard, but would constitute a nuisance, or be aesthetically objectionable, if introduced into the domestic water supply. |

#### Acceptable Backflow Prevention Assemblies for High Hazards

There are several generally accepted types of backflow assemblies that are used for the prevention of backflow for the Health and Non-health conditions.  These are shown in the Table below:

Backflow Protection Devices and Assemblies

Air gap (AG);

Reduced-pressure principle backflow-prevention assembly (RP);

Double check valve assembly (DCVA);

Pressure vacuum breaker (PVB); and

Atmospheric vacuum breaker (AVB).

A Dual Check Valve or Residential Dual Check Valve is not an approved backflow protection assembly and may only be used for protection in cases of premises being served by Reclaimed Water with no other hazards present.

#### Backflow Prevention Devices and Assemblies Application for Health and Non-health Hazards

The minimum acceptable backflow prevention devices and assemblies that may be used for protection against Health and Non-health Hazards are shown in the following table. Where higher levels of toxicity, potential for microbial contamination, or possibilities for interconnection exist a Health Hazard assembly may be required for Non-health Hazards.

| Hazard | Health Hazard |  | Non-health Hazard |  |
| --- | --- | --- | --- | --- |
| #### Backflow Device | Backsiphonage | Backpressure | Backsiphonage | Backpressure |
| Air Gap* | X | X | X | X |
| Reduced Pressure Principle (RP) | X | X | X | X |
| Double Check Valve Assembly (DCVA) |  |  | X | X |
| Pressure Vacuum Breaker (PVB) | X |  | X |  |
| Atmospheric Vacuum Breaker (AVB) | X |  | X |  |

*  Typically, RPBA assemblies are substituted when Air Gaps are not practical.

#### Consideration for Fire Service Lines

Fire service lines may feed internal fire sprinkling systems, hose connections, storage tanks, fire hydrants and other types of suppression systems thus the types of fire suppression is classified on the basis of water source and arrangements of the water supply. AWWA categorizes fire suppression systems into six (6) distinct classes (Class 1 through Class 6.) The description and plumbing for the variety of possible fire suppression plumbing arrangements is beyond the scope of this document and for any fire service line that includes the connection of any plumbing beyond fire sprinkling systems, the reader is referred to AWWA Recommended Practices for Backflow Prevention And Cross-Connection Control M14 and NFPA, Chapter 13.

Fire service lines connected directly to public water mains only where no pumps, tanks, and there are no reservoirs, or physical connection from other water supplies and there are no antifreeze or other additives of any kind and where all sprinkler drains discharge to the atmosphere, dry wells, or other safe drains or outlets may not constitute a health hazard condition.  However, if any of the following conditions exist backflow prevention is required.

Examples of Special Conditions Requiring

Backflow Prevention Assemblies on Fire Sprinkling Systems

- Underground fire sprinkler pipelines parallel to and within 10 ft (3 m) horizontally of sewer pipelines or other pipelines carrying significantly toxic materials.

- When water is supplied to a site or an area from two or more services of a water utility or from two different water utilities.

- Occupancies (or changes in occupancies) that involve the use, storage, or

handling of types and quantities of materials in a manner that could present a significant health hazard to the domestic supply.

- Premises with unusually complex piping systems (usually these premises will have an approved backflow-prevention assembly on their domestic service piping).

- Systems with pumper connections in which non-toxic corrosion inhibitors or other non-toxic chemicals are added to tanks of fire trucks, or where the water purveyor cannot be assured of the potability of the input to the pumper connection.

Source:  AWWA Recommended Practices for Backflow Prevention And Cross-Connection Control M14.

Because of the potential for Cross-Connections from internal plumbing or for consideration of the conditions listed above, backflow prevention assemblies are often required by the water system.  At a minimum, for service lines supplying fire sprinkler systems only, the service line should be protected by a minimum of a Double Check Valve Assembly.

#### Considerations for Backflow Containment

Containment is the installation of an approved backflow prevention assembly at the water service connection to any customer’s premises, where it is physically and economically unfeasible to find and permanently eliminate or control all actual or potential cross-connections within the customer’s water system.  Containment is accomplished by the installation of an approved backflow prevention assembly on the service line leading to and supplying a portion of a customer’s water system where there are actual or potential cross-connections that cannot be effectively eliminated or controlled at the point of the cross-connection.

The following include facilities where containment may be appropriate.

1. Hospitals, mortuaries, clinics, nursing homes, animal hospitals

2. Laboratories

3. Sewage treatment plants, sewage pumping stations, storm water pumping

stations

4. Chemical plants, dyeing plants, metal plating industries, tanneries

5. Petroleum processing or storage plants

6. Slaughterhouses, poultry processing plants, food or beverage processing plants

7. Piers, docks, waterfront facilities

8. Photo development plants

9. Car washes, Laundromats

10. Public swimming pools

11. Where reclaimed water is being provided to the premises.

12. Farms where water is used for other than household purposes

13. Premises with internal cross-connections that are not correctable or with

intricate plumbing arrangements which make it impractical to determine if

cross-connections exist

14. Premises where, because of security requirements or other prohibitions or

restrictions, it is impossible or impractical to make a cross-connection survey.

15. Premises having a repeated history of cross-connections being established or

reestablished.

#### Backflow Isolation and Considerations for Use

Isolation consists of two types, fixture isolation and area or zone isolation. Isolation at a fixture means installing an approved backflow preventer at the source of the potential contamination. Isolation at an area or zone is confining the potential source of contamination within a specific area. Isolation may be appropriate with or without containment depending on the whether the conditions create a health or non-health hazard.

When isolation is appropriate, an approved backflow prevention assembly must be used. The following are examples of isolating the public water supply systems from potential health hazards:

1. Lawn irrigation systems

2. Fire service systems (See AWWA M14 for Classes of Fire Service)

3. Laboratory facilities

Other systems may also need to be isolated with backflow prevention assemblies. Review by the water purveyor will determine the necessity of backflow prevention assembly installation.

Isolation is used for internal protection of systems where both backsiphonage and backpressure may occur. Stopping potential conditions at the source adds additional levels of protection to both customers and the water system.

For a health hazard condition a Reduced Pressure  Principle (RP) is required. In some non-hazard cases a Double Check Valve (DCVA) may be used.

For internal protection where a non-hazard condition exists and back pressure cannot occur, Vacuum Breakers may be used.  Atmospheric Vacuum Breakers (AVB) must be located on the discharge side of the last valve on the line serving the fixture or equipment and must be placed at least six inches above the highest outlet. Atmospheric Vacuum Breakers may not be used where supply pressure is continuous.

Where the AVB is compromised by a shut-off valve downstream, the AVB must be replaced with a Spill Resistant Vacuum Breaker (SVB.) The SVB must be installed at least six inches above the highest outlet.

Pressure Vacuum Breakers (PVB) must be used if a shut-off valve is located on the discharge side of the device or where a vacuum breaker cannot be placed the required distance above the outlet. Pressure Vacuum Breakers may be used where supply pressure is continuous.  PVB must be installed at least twelve inches above the highest outlet. If chemicals are injected into the lawn sprinkler system, a RP must be installed.

Boiler Feed Lines and Laboratories must be isolated from the remainder of the premises with a Reduced Pressure Principle Assembly (RP).

Lawn sprinkler or irrigation systems must be isolated and may be isolated using Vacuum Breakers. If an Atmospheric Vacuum Breaker is used, it must be installed at least 12 inches above the highest sprinkler head.  One AVB is installed on each zone of the sprinkler system. AVP’s and PVB’s should be installed at the highest elevation of the property.

### Selection and Installation of Approved Backflow Prevention Assemblies

#### Air Gap (AG)

An air gap is a vertical, physical separation between the end of a water supply outlet and the flood-level rim of a receiving vessel. This separation must be at least twice the diameter of the water supply outlet and never less than one inch. An air gap is considered the maximum protection available against backpressure backflow or backsiphonage but is not always practical and can easily be bypassed.

An air gap is measured vertically from the lowest end of the supply pipe to the flood level rim or highest possible water level of the fixture or tank into which it discharges. In general, the separation must be twice the supply pipe inside diameter, but never less than one inch. The close proximity of walls or obstructions will necessitate the use of a larger air gap. A larger air gap will also be required if foaming materials are added to the reservoir so that foam does not back up into the supply pipe.

Advantages:

- Very safe and reliable if properly installed and maintained

- Provide maximum protection due to physical separation of potable and

non-potable water

- Easy to inspect

Limitations:

- Easy to bypass or defeat with funnels or hoses

- Supply pressure is lost, requiring reservoir and additional pumping equipment

- Undesirable splashing may occur

- Incoming water may be exposed to airborne contaminants or lose residual

chlorine

Reduced Pressure Principle Backflow Preventer (RP)

A Reduced Pressure Backflow Prevention Assembly may be used to isolate health hazards in place of an Air Gap. It consists of two independently acting check valves, an automatically operated pressure differential relief valve located between the two check valves, and watertight valves located at each end of the assembly, together with four properly located test cocks for testing the operation of the device. This assembly will indicate leakage through one or both check valves or the relief valve by the discharge of water from the relief valve port. During normal operation, both check valves remain closed until there is a demand for water. The differential relief valve remains closed because the inlet pressure is higher than the pressure in the intermediate zone. The second check remains open as water flows through the device. In opening and closing the check valves, the water pressure may be reduced by 4 to 20 psi depending upon the assembly design.

During a backpressure condition, pressure increases downstream of the assembly and both check valves close to prevent backflow. If the second check valve is prevented from closing tightly, leakage back into the zone between the check valves will increase the pressure in the zone and cause the relief valve to open. Water in the zone will then be discharged.

During backsiphonage, the supply pressure drops and the relief valve opens automatically and drains enough water from the zone to maintain pressure in the zone lower than the supply pressure. The second check valve closes to prevent downstream water from draining through the relief valve.

Advantages:

- Protects against both backpressure and backsiphonage

- Can be used under constant pressure

- An RP is effective against backpressure backflow and backsiphonage

- Malfunctioning is easily indicated by discharge of water from the relief valve.

Limitations:

-     Pressure loss of 6-12 psi across the assembly and must be installed above

grade

#### Double Check Valve Assembly (DCVA)

A Dual Check Valve is effective against backpressure backflow and backsiphonage but should be used to isolate only non-health hazards.

A Double Check Valve Assembly consists of two single independently acting check valves with watertight valves located at each end of the assembly, and four properly located test cocks for testing the water tightness of each check valve. During normal operation, both check valves remain closed until there is a demand for water. In the event of backflow, both check valves close preventing reversal of flow.

Two standard plumbing check valves in series may not be used in place of the double check valve assembly due to the necessity for testing.  The Double Check Valve Assembly is an integral assembly designed specifically for backflow prevention.

Advantages:

-     Protect against backflow due to both backpressure and backsiphonage

-     May be used under continuous pressure

-     Little pressure loss occurs across the device

Limitations:

-     No external indication of failure

- May only be used in low hazard situations

#### Residential Dual Check Valve

Dual check valves may not be used for health or high hazards. They are an acceptable solution for preventing potential backflow and backsiphonage for service connections in water service areas that are also served with reclaimed water. They are sized for use on small supply lines (1" or less) and are to be installed immediately downstream of the meter.

Residential Dual Check Valve Backflow Preventers consist of two independently operating check valves. It usually does not include shutoff valves, may or may not be equipped with test cocks or ports, and is generally less reliable than a DCVA. During normal operation, both check valves remain closed until there is a demand for water. In the event of backflow, both checks close to prevent reversal of flow.

Dual Checks may be used for continuous pressure applications and will protect against both backsiphonage and backpressure.

NOTE: Consideration must be given to thermal expansion problems that may arise in the home after installation of a dual check device.

Advantages:

- Protect against both backsiphonage and backpressure in low hazard situations

- May be used under continuous pressure

- Low initial installation cost

- May be Used for Reclaimed Water

Limitations:

- May be used only for residential applications

- No external indication of failure

- Must be replaced at least every 5 years

#### Pressure Vacuum Breaker (PVB)

A PVB may be used to isolate high or low hazards but is effective against backsiphonage only. This assembly is intended to be used under constant pressure conditions.

It is a mechanical backflow preventer that consists of an independently acting, spring-loaded check valve and an independently acting, loaded air inlet valve on the discharge side of the check valve. It includes shutoff valves at each end of the assembly and is equipped with test cocks.

The pressure vacuum breaker uses loading to actuate the atmospheric vent only when backsiphonage occurs or when the line is depressurized.  Two gate valves, test cocks and an additional check are also added. This assembly differs from the atmospheric vacuum breaker in that a spring has been added to the check valve.

Advantages:

- Sometimes less expensive than alternatives

Limitations:

-     Does not protect against backflow due to backpressure.

- May only be used in non-health or low hazard situations

- Cannot be installed if chemicals are used.

#### Atmospheric Vacuum Breaker (APV)

The device usually consists of a float which is free to travel on a shaft and seal in the uppermost position against atmosphere with a disc. Water flow lifts the float, which then causes the disc to seal. When the water supply pressure drops below atmospheric pressure (14.7 psi) the disc will drop down venting the unit to atmosphere and opening the downstream piping to atmospheric pressure, thus preventing backsiphonage. The device is designed to be installed downstream of the last valve in the system and to be operated under pressure for no more than twelve hours in any twenty-four-hour period.

Advantages:

- Inexpensive

Limitations:

-     Does not protect against backflow due to backpressure.

- May only be used in non-health or low hazard situations

- It is a single fixture device

#### Hose Bibb Vacuum Breaker (Isolation)

Hose bibb Vacuum Breakers are not approved for health or  high hazard situations but provide a inexpensive means of isolating potential backsiphonage situation caused by connections of hoses to outside spigots.

The device consists of a spring loaded check valve that seals against an atmospheric outlet when water is flowing.  When the water supply is turned off, the device vents to atmosphere, thus protecting against backsiphonage.

These assemblies are suitable only for isolation in situations where outside spigots may be used to connect hoses.  Hoses pose both non-health and health threats.  Health threats are introduced when water pressure is used in combination with a hose to apply fertilizers or herbicides. Hoses may also be unintentionally submerged in toxic or microbially contaminated liquids that can backsiphone under the right conditions.

Advantages:

- Inexpensive method of isolating hoses

- Isolation of hose problems resolves most customer complaints

Limitations:

- Does not protect against backflow due to backpressure.

- May only be used in for isolation and is not acceptable for protection against

health or high hazards.

-     Will fail to operate properly if there is a shut-off valve installed downstream.

Reference:

West Virginia Cross

Connection Control Manual

### Steps in Establishing an Approved DEP Cross-connection Control Program

#### Step 1 – Establishment of Legal Authority and Development of Cross-Connection Control Policy

Establishing the legal authority is essential for water systems required to implement Cross-Connection Control Programs.  For municipal public water systems an  administrative body must pass an ordinance.  If the system is a non-municipal entity, the governing board must develop and approve a Cross-Connection Control Policy that includes DEP requirements.  The minimum requirements are shown below:

#### Requirements for Legal Authority for CWS

- Develop an Ordinance by legal authority if the CWS is a state permitted municipal agency; or,

- Develop a cross-connection control policy or other legal instrument to establish legal authority for cross-connection control program enforcement if a state permitted CWS.

#### Cross-Connection Control Program Policy Requirements

- Policy establishing requirement for appropriate backflow preventer at service connections constituting hazard to CWS

- Policy regarding material & installation standards for backflow prevention assemblies at service connections

- Policy regarding testing & maintenance of backflow prevention assemblies at service connections

- Policy regarding enforcement (ie, discontinuing water service) for noncompliance.  The Policy shall include the procedures for the elimination or disconnection upon discovery of inadequately controlled or un-protected cross-connections.  These shall include requirements for the appropriate level of backflow protection and for disconnection of service until the problem is corrected.

#### Step 2 - Establishing Policy Requirement for appropriate BFP at service connections constituting hazard to CWS

A designated responsible water system operator(s) must identify all residential, commercial and industrial customers served and tentatively classify the customers as to backflow potential high or low hazards.  After the identification is of the types of health hazards is known a policy can be developed that specifies the type of backflow prevention assemblies that will be required at the service connection for the protection of the public water supply system. The policy must include the following:

#### Cross-connection Control Backflow Prevention Requirements

- Specify categories of customers where a backflow preventer is required at the service connection and specify the appropriate type of backflow preventer for each such category of customers

- Be consistent with, or more stringent than, FDEP rules including AWWA Manual M14 recommendations and FDEP policies

- Per Rule 62-555.360,  Dual Check Valve Assemblies or Residential Dual Check Valves may be installed instead of RP at service connections to residential premises that are served by reclaimed water and have no other hazards requiring a backflow preventer.

- Per AWWARF recommendation & 3rd Edition of AWWA Manual M14, UL listed alarm check valve may be accepted in lieu of a Backflow preventer at service connections to existing fire-protection systems presenting only low hazard with no chemical additives.

- l A backflow prevention assembly may be installed just at service connections to premises having auxiliary water system instead of at all service connections and auxiliary water supply connections.

#### Step 3 -  Establish Policy regarding Material and Installation Standards for Backflow Prevention Assemblies at Service Connections

There are numerous manufactures of backflow prevention assemblies.  However many of these assemblies are not approved for Cross-Connection Control Program applications. It is important that the policy reference only those assemblies that have been approved by AWWA or the Florida Building Code as suitable for use.  It is also important that backflow prevention assemblies be installed properly to maintain their functionality. Below are standards that must be included in a Cross-Connection Control Policy:

#### Standards for Backflow Prevention Assemblies and Methods of Installation

- Specify material standards for Backflow preventers, i.e., for new CWS-owned: Reduced Pressure Principle Assemblies (RP), Double Check Valves Assemblies( DCVA) and must conform to AWWA Standards C510 and C511

- New customer-owned Backflow preventers must conform to applicable standard referenced in the Florida Building Code

- Specify Backflow Preventers installation standards consistent with, or more stringent than, FDEP rules (including AWWA Manual M14 recommendations)

- Backflow preventers must be installed at customer's meter or property line (ie, at point of service.)

- Reduced Pressure Principle Assemblies (RP), Pressure Vacuum Breakers (PVB), Atmospheric Vacuum Breakers (AVB) shall not be installed in below ground pits, but Double Check Valve Assemblies and Residential Dual Check Valves may be installed in below ground pits if test cocks are plugged & adequate drainage is provided to maintain normally dry location.

#### Step 4 -  Establish a Policy for Testing and Maintenance of Backflow Prevention Assemblies at  Service Connections

CWS’ must establish policies for testing and maintenance of backflow prevention assemblies at  service connections. Maintenance and testing of backflow prevention assemblies must be performed by certified backflow prevention assembly testers.  Large municipal agencies may have employees or departments that actually perform the testing and maintenance.  Smaller municipal agencies and permitted water supplies may contract for this service to certified backflow prevention testers.  In either case, the permitted water agency maintains the responsibility for ensuring that the testing and maintenance of backflow prevention assemblies is properly performed.  The testing and maintenance procedures need to identified and documented in a written policy.

Policy for the Testing and Maintenance of Backflow Prevention Assemblies

Schedule for Field Testing and Maintenance of Backflow Assemblies

- Reduced Pressure Principle Assemblies (RP),  Pressure Vacuum Breakers (PVB), Atmospheric Vacuum Breakers (AVB), Double Check Valve Assemblies (DCVA), and certain Residential Dual Check Valve’s (RDC) must be field-tested after installation or repair and tested at least annually

- Reduced Pressure Principle Assemblies (RP), Pressure Vacuum Breakers, Atmospheric Vacuum Breakers, Double Check Valve Assemblies and certain Residential Dual Check Valve’s must be repaired or replaced if they fail field-testing

#### Minimum Qualifications for Backflow Prevention Field Testers

- Successfully complete a minimum of a 32-hour course

- Pass the Backflow Certification written and hands-on exams

- Periodically re-certify at least every 2 years.

- Specify Acceptable Procedures for Field Testing

- Customer owned Reduced Pressure Prinicple Assemblies (RP) and   Double Check Valve Assemblies (DCVA) must be tested in accordance with standards referenced in Florida Building Code

- Requirements must include replacement of Residential Dual Check Valve’s at service connections must be overhauled or replaced at least every 5 years.

- Field testing equipment must be calibrated annually

#### Step 5 -  Procedures for Assessing New and Existing Service Connections to Determine the Need for BFP’s

CWS’ must establish policies for assessing the potential for health or high and non health or low hazards for both new and existing customers.  The methods used can include questionnaires or surveys, field inspections, review of customer applications for water service or change of use or ownership that requires a permit from a government agency.

When new building construction permits are issued by the local permitting agency, plans must be reviewed from a cross-connection control perspective and address cross-connection protection.  This will avoid potential arguments when water service application is made.

When application for service is made by the customer, use of the appropriate backflow prevention device or assembly should be confirmed by the reviewer in accordance with the degree of hazard at the service connection.

Procedures should also include follow-up site inspection when the construction is

completed.  The BFP should be inspected to ensure that it has been properly installed. Fire protection systems must also be inspected to protect against these potential sources of cross-connections.

For multi-use developments where the ultimate hazard is unknown the designer of the plumbing systems must address the use of a Reduced Pressure Principle backflow preventer.  Care should be taken in sizing to ensure that its does not reduce fire protection ratings or reduce domestic water main pressures below the minimum needed.  Typically the size of the BFP should match the size of the water main.

For domestic water, backflow preventors must be the approved type per FAC 62-555.360.

For fire protection systems, Double Check Valves must meet AWWA C510 and Reduced Pressure Principle Backflow Preventers must meet AWWA C511.

Below are the minimum requirements that should be included in a backflow prevention assessment policy.

#### Procedures for Assessing New and Existing Service Connections

- Specify how and when to assess for new and existing service connections

- New Service Connections shall be assessed when application for service is made

- Existing service connections shall be assessed initially according to reasonable schedule and should be assessed whenever an application is received for changing the customer of record.

- Questionnaires may be used for identification of existing service connection requirements and confirmed by a follow-up inspection

When surveys are used, it is highly advisable to schedule the survey of health or high hazard facilities first.  Notify the facilities of pending inspections and schedule the dates that are satisfactory to all parties. After the completing the health or high hazard facilities, survey non-hazard or low hazard sites next. This will alert the water provider to the most serious health concerns at the earliest date.

If a site is tentatively classified as a Health or High Hazard facility, and your inspection verifies that it is truly a Health or High Hazard site, then an approved air gap or approved reduced pressure principle backflow prevention assembly (RP) is required:

For Health or High Hazard sites, if the RP or air gap is located within the plumbing system, the establishment must be re-inspected annually by the local water utility to verify that plumbing connections have not been made upstream of the containment device.

#### Requirements for Testing by type of Backflow Assemblies:

- High Hazard assemblies must be tested yearly

- Non-testable Dual Check Valve Assemblies must be replaced every five years

- Improperly functioning backflow preventers shall be promptly repaired in accordance with the DEP requirements and the water utility shall take appropriate actions in accordance with their local ordinance or other legal instrument.

  - Low hazard establishments must be re-inspected every five years to ensure the classification has not changed.

  - All backflow prevention assemblies required by the CCCP should be inspected (and where applicable tested) within 10 days of initial installation and tested in accordance with the CWS’s written requirements thereafter by a certified tester

  - Elimination or disconnection upon discovery of inadequately controlled or protected cross-connections. These shall include requirements for the appropriate level of backflow protection and for disconnection of service until the problem is corrected.

#### Step 6 – Establish a Procedure for Cross-Connection Control Records

A records management program is essential for a Cross-Connection Program to run efficiently. Records provide accountability, so that customers understand what the agency does and the reasons for actions that may affect them.  It is important to have a written set of policies and procedures so that actions are proper and consistent and those responsible understand the expectations.

Records serve as a collective memory and offer future users details about the decisions that were made.  Records are created to document business transactions and pertinent events such as testing and maintenance information on the backflow assemblies.

Records document these decisions and processes.  Records also protect the legal rights of the agency in case of a contamination problem.

The foundation of any records management program is the development of written policies and procedures.  The essential Policies and Procedures for a Cross-Connection Control Program are shown below:

#### Essential Policy for a Cross-Connection Control Program

- Designate the person assigned primary responsibility for administering the CCC Program

- List all customers served by the CWS.

#### Type and Format of Records to be Maintained

- Keep all completed service connection assessment questionnaires or reports or keep paper or computer summaries of this information

- List of all customers with backflow prevention assemblies.

- List pertinent information about each BFP’s, i.e., size, make, model, location, etc.

- Keep all actual BFP test reports, i.e., completed service connection assessment, annual retest date, and test reports or keep paper or computer summaries of this information.

Records retention requirements are set by State Statutes.  Below are the retention requirements for Cross-Connection Control Program requirements.

#### Records Retention Requirements

- Service Connection Assessment records and BFP test records must be kept for 10 years.

- Records must be maintained by the CWS and made available to DEP during the sanitary surveys of the water utility.

- Actual Service Connection Assessment Questionnaire should be kept indefinitely and should contain signed statement concerning the customer’s water use.

#### Step 7 – Establish Procedures for Enhanced Public Education and Inspection Enhancement

Enhanced public education efforts towards prevention of cross-connections and enhanced inspection programs for portions of the distribution system in areas of reuse for detection and elimination of cross-connections specific to reuse systems are required by state statute.  It is recommended that all community water systems provide customers with backflow prevention education. Education is essential in identifying and removing health threats to the CWS.  A public education policy is provided below:

#### Public Education Policy and Procedures for Cross-Connection Control

- Specify how and when enhanced public education will be provided

- Procedures for Systems that use Reclaimed Water Systems and permit Dual Check Valves at service connections at residential premises must adhere to all the following (Rule 62-555.360(4)(f) and (5)(b).

- Educational brochures should be distributed to customers every 2 to 5 years, and should be provided on-site at displays and through media coverage such as public service announcements and newspaper articles.

- CWS should distribute educational brochures to customers when:

    - When Dual Check Valve is originally installed or when application is made for new service to premises with Dual Check Valve

    - When application is made for change in customer of record at premises with Dual Check Valve

Reference:

John Sowerby, DEP

2006 FWRA Focus On Change

### FAC 62.555.360 - Cross-Connection Control for Public Water Systems

62-555.360 Cross-Connection Controls for Public Water Systems.

(1) Cross-connection, as defined in Rule 62-550.200, F.A.C., is prohibited. However, a person who owns or manages a public water system may interconnect to another public water system if that system is operated and maintained in accordance with this chapter.

(2) Community water systems, and all public water systems that have service areas also served by reclaimed water systems regulated under Part III of Chapter 62-610, F.A.C., shall establish and implement a routine cross-connection control program to detect and control cross-connections and prevent backflow of contaminants into the water system. This program shall include a written plan that is developed using recommended practices of the American Water Works Association set forth in Recommended Practice for Backflow Prevention and Cross-Connection Control, AWWA Manual M14, as incorporated into Rule 62-555.330, F.A.C.

(3) Upon discovery of a prohibited cross-connection, public water systems shall either eliminate the cross-connection by installation of an appropriate backflow prevention device acceptable to the Department or shall discontinue service until the contaminant source is eliminated.- 384

(4) Only the following are considered to be backflow prevention devices. They shall be installed in agreement with and under the supervision of the supplier of water or his designated representative (plumbing inspector, etc.) at the consumer’s meter, at the property line of the consumer when a meter is not used, or at a location designated by the supplier of water or the Department. The devices are:

(a) Air gap separation – A physical separation between the free-flowing discharge end of a potable water supply pipeline and an open or non-pressure receiving vessel. An “approved airgap separation” shall be at least double the diameter of the supply pipe measured vertically above the top of the rim of the vessel. In no case shall it be less than 1 inch.

(b) Reduced pressure backflow preventer – A device containing within its structure a minimum of two independently acting approved check valves, together with an automatically operating pressure differential relief valve located between the two check valves. The first check valve reduces the supply pressure a predetermined amount so that during normal flow and at cessation of normal flow the pressure between the checks shall be less than the supply pressure. In case of leakage of either check valve, the differential relief valve, by discharging to the atmosphere, shall operate to maintain the pressure between the checks less than the supply pressure. The unit shall include tightly closing shutoff valves located at each end of the device, and each device shall be fitted with properly located test cocks.

(c) Atmospheric vacuum breaker – A backflow prevention device which is operated by atmospheric pressure in combination with the force of gravity. The unit is designed to work on a vertical plane only. The one moving part consists of a poppet valve which must be carefully sized to slide in a guided chamber and effectively shut off the reverse flow of water when a negative pressure exists.

(d) Pressure vacuum breaker – A pressure vacuum breaker is similar to an atmospheric vacuum breaker except that the

checking unit poppet valve is activated by a spring. This type of vacuum breaker does not require a negative pressure to react and can be used on the pressure side of a valve.

(e) Double check valve assembly – An assembly composed of two single, independently acting, check valves, including tightly closing shutoff valves located at each end of the assembly and suitable connections for testing the water tightness of each check valve. A check valve is a valve that is drip-tight in the normal direction of flow when the inlet pressure is one psi and the outlet pressure is zero. The check valve shall permit no leakage in a direction reverse to the normal flow. The closure element (e.g., clapper) shall be internally weighted or otherwise internally loaded to promote rapid and positive closure.

(f) Residential Dual Check – A compact unit manufactured with two independent spring actuated check valves. The residential dual check is acceptable only as added back-flow prevention in areas served by reuse systems defined in Chapter 62-610, Part III, F.A.C., when the cross-connection control program identifies activities specific to paragraphs (5)(a) and (5)(b) of this section.

(5) Cross-connection control programs specific to reuse systems defined in Chapter 62-610, Part III, F.A.C., shall consider the following:

(a) Enhanced public education efforts towards prevention of cross-connections.

(b) Enhanced inspection programs for portions of the distribution system in areas of reuse for detection and elimination of cross-connections.

(c) Dual check valves shall be considered acceptable for reducing risks from back-flow only at residential properties served by reclaimed water unless:

1. Local codes, ordinances, or regulations require greater levels of back-flow prevention.

2. Other hazards exist on the property that require a greater level of back-flow prevention.

Specific Authority 403.086(8), 403.861(9) FS. Law Implemented 403.086(8), 403.855(3) FS. History–New 11-19-87, Formerly 17-22.660, Amended 1-18-89, 1-3-91, 1-1-93, Formerly 17-555.360, Amended 8-28-03.

Water System Employees and Contractors

All Employees/operators of the water system shall read this policy and provide assurance to the owner that he/she has an understanding of cross-connection prevention requirements.

All employees of the water system shall be sensitive to cross-connect control.  Meter readers and system operators will be instructed in cross-connection control and will be required to be on the alert for potential cross-connections in the course of their daily work activities.

The system operator will at minimum, survey the water system during the months of July and January of each year for the specific purpose of locating cross-connections or potential cross-connections.  Surveys during other times will be conducted whenever potential cross-connections have been reported or are suspected.

Listing of Plumbing Connection that Can Potentially Cause Cross-Connections

The following is a partial list of the types of fixtures that can have cross-connections and could pose a hazard to the potable water supply.

1.      Agricultural mixing tanks

2.	Auxiliary water supply

3.	Dialysis equipment

4.      Dishwashers

5.      Garden hoses

6.      Fire Protection Systems

7.      Lawn Irrigation Systems

8.      Photographic developers

9.	Sinks

10.    Solar Energy systems

11.    Swimming pools

12.   Toilet flush valves

13.   Watering troughs

14.   Water softeners

If cross-connection potentials are identified resulting from the above, the source of the cross-connection will be eliminated.

Common Problems to be evaluated for Cross-Connection Potential

Water systems employees and contractors will be instructed that a cross-connection can appear to be simply a hose, pipe, or any water outlet with no specific or outstanding features.  The real distinction is where the connection leads.  It is a cross-connection if it leads from a potable line to anything other than potable service.  For example, water softeners form a cross-connection that is not normally hazardous.  However, when the drain is connected directly to the sanitary sewer, it becomes potentially very hazardous.

Requirements for Reporting Cross-Connections

Anyone observing a cross-connection or potential cross-connection in the ____________
___________________ Water System shall first point out the problem and discuss the significance with the customer.  He/She shall then report the occurrence to the owner of the water system, in writing.  The licensed operator shall be responsible for assuring that all cross-connections or potential cross-connections are inspected and corrected in a timely manner.

Cross-Connection Control and Protection

Upon discovery of prohibited or inadequately controlled or protected Cross-Connection hazard, the hazard shall be eliminated by ensuring that the appropriate backflow prevention device(s) or assembly(s) are installed or service to the customer shall be discontinued until the hazard has been eliminated.

Name and Location of CWS:

_________________________________________

_________________________________________

_________________________________________

Legal Authority/Owner of CWS

_________________________________________

Date:_____________________________

### Frequently Asked Questions

- What is back siphonage?

Back siphonage is the reversal of normal flow in a system caused by a negative pressure (vacuum or partial vacuum) in the supply piping.

- What factors can cause back siphonage?

Back siphonage can be created when there is stoppage of the water supply due to nearby fire fighting, repairs or breaks in city main, etc.  The effect is similar to the sipping of an ice cream soda by inhaling through a straw, which induces a flow in the opposite direction.

- What is backpressure ?

Backpressure is the reversal of normal flow in a system due to an increase in the downstream or customer’s pressure above that of the supply pressure

- What factors can cause a backpressure condition?

Backpressure is created whenever the downstream pressure exceeds the supply pressure, which is possible in installations such as heating systems, elevated

tanks, and pressure-producing systems.  An example would be a hot water space-heating boiler operating less than 15-20 lbs. Pressure coincidental with a reduction of the city water supply below such pressure (or higher in most commercial boilers).  As water tends to flow in the direction of least resistance, a backpressure condition would be created and the contaminated boiler water would flow into the potable water supply.

- What is a cross-connection?

A cross-connection is a direct arrangement of a piping line which allows the potable water supply to be connected to a line which contains a contaminant.  An example is the common garden hose attached to a sill cock with the end of the hose lying in a cesspool. Other examples are a garden hose attached to a service sink with the end of the hose submerged in a tub full of detergent, supply lines connected to bottom-fed tanks, supply lines to boilers.

- What is the most common form of a cross-connection?

Ironically, the ordinary garden hose is the most common offender as it can be easily connected to the potable water supply and used for a variety of potentially dangerous

applications.

- What is potentially dangerous about an unprotected outside spigot or sill cock?

The purpose of a sill cock is to permit easy attachment of a hose for outside watering purposes.  However, a garden hose can be extremely hazardous because they are left submerged in swimming pools, lay in elevated locations (above the sill cock) watering shrubs, chemical sprayers are attached to hoses for weed-killing,

etc.; and hoses are often left lying on the ground which may be contaminated with fertilizer, cesspools, and garden chemicals.

- What protection is required for sill cocks?

A hose bibb vacuum breaker should be installed on every sill cock to isolate garden hose applications thus protecting the potable water supply from contamination.

Should a hose bibb vacuum breaker be used on frost-free hydrants?  Definitely, providing the device is equipped with means to permit the line to drain after the hydrant is shut-off. A “removable” type hose bibb vacuum breaker could allow the hydrant to be drained, but the possibility exists that users might fail to remove it for

draining purposes, thus defeating the benefit of the frost-proof hydrant feature.  If the device is of the “Non-Removable” type, be sure it is equipped with means to drain the line to prevent winter freezing.

- Can an atmospheric, anti-siphon vacuum breaker be installed on a hose bibb?

Theoretically yes, but practically no.  An anti-siphon vacuum breaker must be elevated above the sill cock to operate properly. This would require elevated piping up to the vacuum breaker and down to the sill cock and is normally not a feasible installation.  On the other hand, a hose bibb vacuum breaker can be attached directly to the sill cock, without plumbing changes and at minor cost.

- What is an atmospheric vacuum breaker?

The most commonly used atmospheric anti-siphon vacuum breakers incorporate an atmospheric vent in combination with a check valve.  Its operation depends on a supply of potable water to seal off the atmospheric vent, admitting the water to downstream equipment. If a negative pressure develops in the supply line, the loss of pressure permits the check valve to drop sealing the orifice while at the same time the vent opens admitting air to the system to break the vacuum.

- Will an anti-siphon vacuum breaker protect against a backpressure condition?

Absolutely not!  If there were an increase in the downstream pressure over that of the supply pressure, the check valve would tend to “modulate” thus permitting the backflow of contaminated water to pass through the orifice into the potable water supply line.

- Can an atmospheric vacuum breaker be used on lawn sprinkler systems?

Yes, if these are properly installed, they will protect the potable water supply. The device shall be installed 6" above the highest sprinkler head and shall have no control valves located downstream from the device.

- Can an atmospheric vacuum breaker be used under continuous pressure?

No! Codes do not permit this as the device could become “frozen”, and not function under an emergency condition.

- Can a pressure vacuum breaker be used on a multi-zone lawn sprinkler system?

Yes. This type of vacuum breaker can be used under continuous pressure.  Therefore, if properly installed, it will protect the potable water supply. The assembly shall be installed 12" above the highest sprinkler head.

- What is continuous pressure?

This is a term applied to an installation in which the pressure is being supplied continuously to a backflow preventer for periods of over 12 hours at a time. Laboratory faucet equipment, for example, is entirely suitable for a non-pressure,

atmospheric anti-siphon vacuum breaker because the supply is periodically being turned on and shut off.  A vacuum breaker should never be subjected to continuous pressure unless it is of the continuous pressure type and clearly identified for this service.

- Are check valves approved for use on boiler feed lines?

Most jurisdictions require backflow protection on all boiler feed lines.  Some will allow a backflow preventer with intermediate vent as minimum protection for residential boilers. A reduced pressure backflow preventer is generally required on commercial and compound boilers.  However, low cost, continuous pressure backflow preventers are now available which will perform with maximum protection; thus check valves are not recommended.

- What is the difference between pollution and contamination?

Pollution of the water supply does not constitute an actual health hazard, although the quality of the water is impaired with respect to taste, odor or utility.  Contamination of the water supply, however, does constitute an actual health hazard; the consumer being subjected to potentially lethal water borne disease or illness.

- What does “Degree of Hazard” mean?

The degree of hazard is a commonly used phrase utilized in cross-connection programs and is simply a determination on whether the substance in the non-potable

system is toxic (health hazard) or non-toxic (non-health hazard).

- What is the difference between a toxic and a non-toxic substance?

Toxic substance is any liquid, solid or gas, which when introduced into the water supply creates, or may create a danger to health and well being of the consumer.  An

example is treated boiler water.  A non-toxic substance is any substance that may create a non-health hazard, is a nuisance or is aesthetically objectionable, i.e., foodstuff, such as sugar, soda pop, etc.  Therefore, you must select the proper device or assembly according to the type of connection and degree of hazard.  There are five basic products that can be used to correct cross-connection.

- What are the five basic products used for protection of cross-connections?

The five basic products are:

1. Air Gap

2. Atmospheric Vacuum Breakers -which also includes hose connection vacuum breakers

3. Pressure Vacuum Breakers

4. Double Check Valve Assembly

5. Reduced Pressure Principle Backflow Preventers

- What is an Air Gap and where is it used?

Air Gap is the physical separation of the potable and nonpotable system by an air space.  The vertical distance between the supply pipe and the flood level rim should be two times the diameter of the supply pipe, but never less than 1". The air gap can be used on a direct or inlet connection and for all toxic substances.

Because today’s complex plumbing systems normally require continuous pressure, air gap applications are actually in the minority.  It should be remembered, however, that whenever a piping terminates a suitable distance above a contaminant, this itself is

actually an air gap.  Air Gaps are frequently used on industrial processing applications, but care should be taken that subsequent alterations are not made to the piping, which would result in a direct connection.

- Where is an Atmospheric Vacuum Breaker used?

Atmospheric Vacuum Breakers may be used only on connections to a non-potable system where the vacuum breaker is never subjected to backpressure and is installed on the discharge side of the last control valve.  It must be installed above the usage point.  It cannot be used under continuous pressure.

- Where is a Hose Bibb Vacuum Breaker used?

Hose Bibb Vacuum Breakers are small inexpensive devices with hose connections, which are simply attached to sill cocks and threaded faucets or wherever there is a possibility of a hose being attached which could be introduced to a contaminant. However, like the Atmospheric Vacuum Breaker they should not be used under continuous pressure.  Remember, no shut-off valves are permitted downstream!

- Where is a Pressure Vacuum Breaker used?

Pressure Vacuum Breakers may be used as protection for connections to all types of non-potable systems where the vacuum breakers are not subject to backpressure. These units may be used under continuous supply pressure.  They must be installed above the usage point. (Spill resistant models for indoor use are also available).

- Where is a Backflow Preventer with Intermediate Atmospheric vent used?

These devices are made for 1⁄2" and 3⁄4" lines feeding residential boilers. In addition,  they provide the added advantage of providing protection against backpressure in low hazard applications.

- Where is a Double Check Valve Assembly used?

A double check valve assembly may be used as protection of all direct connections through which foreign material might enter the potable system in concentration, which would constitute a nuisance, or be aesthetically objectionable, such as air, steam, food, or other material which does not constitute a health hazard.

- What are typical applications for Atmospheric Vacuum Breakers?

Atmospheric Vacuum Breakers can be used on most inlet type water connections which are not subject to backpressure such as low inlet feeds to receptacles containing toxic and non-toxic substances, valve outlet or fixture with hose attachments, lawn sprinkler systems and commercial dishwashers.

- What are typical applications for Hose Bibb Vacuum Breakers?

Hose Bibb Vacuum Breakers are popularly used on sill cocks, service sinks and any threaded pipe to which a hose may potentially be attached.

- What are typical applications for Pressure Vacuum Breakers?

These applications should be similar to the Atmospheric Vacuum Breaker with the exception that these may be used under continuous pressure. However, they should not be subject to backpressure.

- What are typical applications of Backflow Preventer with Intermediate Vent?

For 1⁄2" and 3⁄4" lines these devices are popularly used on low hazard boiler feed water supply lines, cattle drinking fountains, trailer park water supply connections and other similar low-flow applications.  They will protect against both backsiphonage and backpressure and can be used under continuous pressure.

- Where is a Reduced Pressure Zone Backflow Preventer used?

Reduced Pressure Principle Assemblies may be used on all direct connections which may be subject to backpressure or back siphonage, and where there is the possibility of contamination by the material that does constitute a potential health hazard.

- What are typical applications for Double Check Valve Assemblies?

Double Check Valve Assemblies may be used where the degree of hazard is non-health, or low hazard meaning that the nonpotable source is polluted rather than contaminated. The degree of hazard is oftentimes determined by local Inspection Departments and, therefore, such departments should be questioned in order to comply with local regulations.

- What are typical applications for Reduced Pressure Zone Backflow Preventers?

This type should be used whenever the non-potable source is more of a contaminant than a pollutant.  Basically, they are applied as main line protection to protect the municipal water supply, but should also be used on branch line applications where non-potable fluid would constitute a health hazard, such as boiler feed lines, commercial garbage disposal systems, industrial boilers, etc.

- Are there any regulations in OSHA regarding cross-connections?

Yes, OSHA requires that no cross-connection be allowed in an installation unless it is properly protected with an approved backflow preventer.  These requirements are

also covered in B.O.C.A., Southern Standard Building Code, Uniform Plumbing Code, IOC, UPC, and City, State and Federal Regulations.

- What Standards are available governing the manufacture of backflow prevention assemblies?

Reduced Pressure Backflow Prevention Assemblies, Double Check Valve Assemblies, Pressure Vacuum Breakers and Atmospheric Breakers are specified by USC Foundation for Cross-connection Control, ANSI/AWWA and ASSE.  Dual Check Valves and Hose Bibbs are specified by the ASSE Standards.  Various manufactures carry backflow prevention devices meeting these standards, including Cla-Val, Febco, Hersey, Watts and Ames.

- What is the benefit of a strainer preceding a backflow preventer?

A strainer will protect the check valves of a backflow preventer from fouling due to foreign matter and debris, which may be flowing through the line.  This not only protects the valve but also eliminates nuisance fouling and subsequent maintenance and shutdown. The use of a strainer with a water pressure reducing valve has been an accepted practice for years.  The amount of pressure drop attributed to the strainer is negligible and is far outweighed by the advantages provided by the strainer.

- What would cause a reduced pressure backflow preventer to leak?

Leakage from a backflow preventer is normally attributed to foreign matter lodging on the seating area of either the first or second check valve.  Most times this can be corrected by simply flushing the valve, which will dislodge any loose particles. It is, therefore, most important on new installations that the piping be thoroughly flushed before installing the unit.  It should be remembered, however, that spillage does provide a “warning signal” that the valve is in need of maintenance..

- Is periodic testing required for reduced pressure backflow preventers?

Yes, and this is to ensure that the valve is working properly and is a requirement of many states and cross-connection control programs.  Test cocks are provided on the valve for this purpose and manufacturers are required to furnish field testing information.

- Should a backflow preventer be installed in the water supply line to each residence?

Because of the growing number of serious residential backflow cases, many water purveyors are now requiring the installation of approved dual check valve backflow

preventers at residential water meters.  They are also educating the public concerning cross-connections and the danger of backflow into the local water supply. Since water purveyors cannot possibly be responsible for or monitor the use of water within a residence, the requirements for these cross-connection control programs are increasing throughout the country.

- What is a cross-connection control program?

This is a combined cooperative effort between plumbing and health officials, waterworks companies, property owners and certified testers to establish and administer guidelines for controlling cross-connections and implementing means to ensure their enforcement so that the public potable water supply will be protected both in the city main and within buildings.  The elements of a program define the type of protection required and responsibility for the administration and enforcement. Other elements ensure continuing education programs.

- What are the concerns with thermal expansion and backflow prevention?

#### Since backflow prevention devices prevent the exchange of water between the customer and the public water provider that prevents thermal expansion, a pressure blow-off valve must be provided at the hot water tank. Blow-off water should be directed to a proper drain. Gas fired hot water tanks have a tendency to build pressures quickly and these pressures can rupture internal plumbing. Customers are advised to contact a local plumber to correct these situations.

- What are the concerns with freezing and backflow prevention?

#### When temperatures are expected to fall below 32o F for several hours, standing water in unprotected backflow prevention devices can freeze and cause the device to rupture. Above ground non-protected backflow prevention devices should be wrapped in insulating material and/or covered to prevent freezing. Water that is kept in motion (by running the water continuously) will not freeze but this solution can be costly.

#### Appendix 1 – 	Notification to Customer

Intent to Perform Inspection of Existing Connections to CWS

In accordance with Florida Administrative Code 62-555.360 the _________(CWS) must ensure that there are no interconnections that can possibly back feed into the water system.

A program of cross-connection inspection and control has been initiated to provide for reasonable protection of the public drinking water from possible contamination caused by backpressure or backsiphonage conditions on your premises that might cause contamination to the public drinking water.

To assist you with identifying actual or potential cross-connections on your premises, a cross-connection inspector will contact you in the near future to arrange for a time when an inspection can be made of your water system connection.  Following the inspection, you will receive a written report of any significant findings.

Yours very truly,

(Authorized Agent CWS)

Appendix  2 - 	Notification to Customer of Inspection and

Findings of Violation of Cross-Connection Program

Dear _____________ (Customer)

On the above referenced date, personnel from the _____________ (CWS) _______________________________ made an inspection of the water facilities on your premises for the purpose of detecting any existing or potential cross-connections to the public water supply.

The inspection revealed that some revisions, as indicated on the attached sheet, must be made to protect the (CWS).  However, it should be pointed out that our inspection is not an absolute guarantee that all cross-connection hazards have been located.

Provisions of the City of _____________________________ “Cross-Connection Control-General Policy”, and FAC 62-555.360 prohibit the existence of cross-connections within the public water supply.  Since the (CWS) is committed to ensuring the safety of the public’s water, in the future, periodic inspections will be made to determine if your on-site water facilities are in compliance with these laws.

If you have any question, please give me a call between 8:00 A.M. and 3:00 P.M. at

Yours very truly,

(Authorized Agent CWS)

#### Appendix  3 -  	Cross-Connection Survey Form

Commercial, Industrial and Institutional

Date: ____________________       Inspector: _________________________________

Name of Company, Corporation, or Business: ______________________________________________________________________

______________________________________________________________________

Address: ______________________________________________________________________

Name of Contact: ______________________________________________________________________

Type of Use: Industrial _________ Commercial _________ Governmental _________ Other _______                                 SIC ___________

Location of Service: ______________________________________________________________________

Size of Service: _____________________inch               Metered? Yes ?No

Require non-interrupted water service? 				Yes ?No

Does Boiler Feed utilize chemical additives? 			Yes ?No

Is Backflow protection incorporated? 				Yes ?No

Are air conditioning cooling towers utilized? 				Yes ?No

Is Backflow protection incorporated? 				Yes ?No

Is a Water Saver utilized on condensing lines or cooling towers? 	Yes ?No ?N/A

Is the make-up supply line backflow protected? 			Yes ?No

Is process water in use; Is it potable supply water or “Raw” water? Yes ?No ?

(if “Yes” check appropriate) Potable ?Raw ?Protected ?Unprotected

Is fire protection water separate from the potable supply? 		Yes ?No

Are Containment Assemblies in place? 				Yes ?No

Summary

Degree of Hazard: 	High ?	Low

Type of Assembly recommended for containment:   RPZ     DCV ?   None

Fixture Outlet protection required? 	Yes ?		No

If so, where? ___________________________________________________________

______________________________________________________________________

#### Appendix 4  – 	Backflow Prevention Device

Test and Maintenance Report

To: ______________________________________________________________________

(water purveyor or regulatory agency)

______________________________________________________________________

______________________________________________________________________

The cross-connection control assembly detailed hereon has been tested and maintained as required by the (rules or regulations) of (purveyor or regulatory agency) and is certified to comply with these (rules or regulations).

Make of assembly ________________ size ___________________________________

Model Number ________________ located at ______________________________

Serial Number ________________                  ______________________________

| Type | Reduced Pressure Assemblies |  |  | Pressure Vacuum Breaker |  |
| --- | --- | --- | --- | --- | --- |
| Date _____ | Double Check Assemblies |  | Relief Valve | Air Inlet | Check Valve |
|  | 1st Check | 2nd Check |  | Opened ___ psid Did not Open ___ | ____ psid Leaked ___ |
| Initial Test | DC – Closed Tight __ RP ___ psid Leaked ___ | Closed Tight __ Leaked __ | Opened ___ psid |  |  |
| Repairs and Matls. Used |  |  |  |  |  |
| Test After Repairs | DC – Closed Tight __ RP ____ psid | Closed Tight __ | Opened ___ psid | Opened ___ psid | ___ psid |

The above is certified to be true.             Date: _______________

Firm Name _____________________________________________________________ 

Address _______________________________________________________________

Certified Tester _____________________________Cert. Tester No. ________________

#### Appendix 5  – 	Notice to Customer

#### Requirements for Backflow Prevention Inspection

Dear Customer:

Our records indicate that your Backflow Prevention Assembly is due for testing and inspection on (date) _______________________________________________.

To prevent possible contamination of the (CWS), FAC 62-555.360 requires that your backflow prevention assembly be inspected and tested yearly. It is your responsibility to have this test completed.

A list of certified backflow prevention testing companies is attached to this notice. Should you choose to use one of these companies they will perform the inspection and testing and provide this office with a copy of the test results.

It you choose to use another certified tester to perform the inspection and testing of your device, please provide a certified copy of the results to this office.

We appreciate your cooperation and look forward to receiving the results of your testing and inspection soon.

Sincerely,

(Authorized Agent CWS)

#### Appendix  6 – 	Notice to Customer

#### Requirements for Backflow Prevention Replacement

Dear Customer:

Our records indicate that your Backflow Prevention Device or Assembly is due for replacement on (date) _______________________________________________.

To prevent possible contamination of the (CWS),  FDEP requires that your particular backflow prevention device or assembly be replaced every five years.  It is your responsibility to have this device or assembly replaced.

A list of certified backflow prevention testing companies is attached to this notice. Should you choose to use one of these companies they will replace the device or assembly and provide this office with a copy of the completed installation.

If you choose to use another certified tester to perform the replacement your device or assembly, please provide a certified copy of the results to this office.

We appreciate your cooperation and look forward to receiving the confirmation that your backflow prevention device or assembly has been replaced.

Sincerely,

(Authorized Agent CWS)

#### Appendix 7 - 	FWRA Cross-Connection Control Program – Model Ordinance

CROSS-CONNECTION CONTROL PROGRAM

ORDINANCE NO. _______

BE IT ORDAINED BY THE CITY COUNCIL OF THE CITY OF

_________________________________________________________,  FLORIDA:

##### SECTION 1.	PURPOSE

The purpose of this Article is:

(a)       To protect the public water main against actual or potential cross-connections, backflow by backpressure and bicksiphonage by isolating within the premise or private property contamination or pollution that has occurred or may occur because of same un-discovered or unauthorized cross-connection on the premises or private property.

(b)      To protect the water supply system within the premise or private property against actual or potential cross-connections, backflow by backpressure and bicksiphonage by requiring such air gaps, vacuum breakers, backflow preventers, special devices as required by this Ordinance, or other applicable regulations.

(c)      To eliminate cross-connections, backflow by backpressure and bicksiphonage on any other source of water or process water used for any purpose whatsoever which may jeopardize the safety of the water supply or which may endanger the health and welfare of the general public.

(d)      To establish a cross-connection control and backflow prevention program that includes provisions for inspection and maintenance to ensure compliance.

SECTION 2.	RESPONSIBILITY:

The Director of Utilities, or his/her designee, shall be responsible for the protection of the public potable water distribution system from contamination or pollution due to backflow of contaminants or pollutants through the water service connection.  If, in the judgment of said Director, or his designee, an approved backflow prevention assembly is required, at the city's water service connection to any customer's premises, for the safety of the water system, the Director, or his designated agent, shall give notice in writing to said customer to install such an approved backflow prevention assembly at each service connection to his premises.  The customer shall immediately install such approved device, or devices, or assemblies at his own expense; and, failure, refusal, or inability on the part of the customer to install said device, or assemblies, immediately shall constitute a ground for discontinuing water service to the premises until such device, or assemblies, have been properly installed. Cross-connection control devices or assemblies shall comply with FAC 62.555.360.

SECTION 3.		DEFINITIONS:

(a)      Approved:	Accepted by the Director of Utilities or his designee, as meeting an applicable specification stated or cited in this Ordinance, or as suitable for the proposed use.

(b)      Auxiliary Water Supply:	Any water supply on or available to the premises other than the purveyor’s approved public potable water supply.  These auxiliary waters may include water from another purveyor’s public potable water supply or any natural source(s) such as well, spring, river, stream, harbor, etc., or “used waters” or “industrial fluids”.  These waters may be polluted or contaminated or they may be objectionable and constitute an unacceptable water source over which the water purveyor does not have sanitary control.

(c)      Backflow: The flow of water or other liquids, mixtures or substances under pressure into the distributing pipes of a potable water supply system from any source or sources other than its intended source.

(d)  Backpressure:   A pressure, higher than the supply pressure, caused by a pump, elevated tank, boiler, or any other means that may cause backflow.

(e)    Backsiphonage:	The flow of water or other liquids, mixtures or substances into the distributing pipes of a potable water supply system from any other source other than its intended source caused by the sudden reduction of pressure in the potable water supply system.

(f)  Backflow prevention assembly—A mechanical backflow preventer (i.e., SVB, PVB, DCVA, RP), used to prevent the backward flow of contaminants or pollutants into a potable water distribution system.  An assembly has a resilient seated, full-flow shut-off valve before and after the backflow preventer making it testable in-line.  The assembly is shipped with the shut-off valves attached to the backflow preventer.  An assembly is labeled with the manufacture's symbol, size, serial number, model number, the working pressure, and the direction of flow.  The Foundation for Cross Connection Control and Hydraulic Research at the University of Southern California tests and approves backflow prevention assemblies.

(g)   Backflow Prevention Device	 a means of backflow protection, usually mechanical that does not require shut-off valves and test cocks. Any backflow prevention assembly without the shut-off valves is called a device.  The American Society of Sanitary Engineers (ASSE) approves backflow prevention devices.

(h)       Backflow Preventer:	A device, assembly or means designed to prevent backflow. These devices or assemblies are described below:

- Air-Gap:	A physical separation between the free-flowing discharge end of a potable water supply pipeline and an open or non-pressure receiving vessel. An “approved air gap separation” shall be at least double the diameter of the supply pipe measured vertically above the top of the rim of the vessel. In no case shall it be less than 1 inch. When an air-gap is used at the service connection to prevent the contamination or pollution of the public potable water system, an emergency by-pass shall be installed around the air0gap system and an approved reduced pressure principle assembly shall be installed in the by-pass system.

- Approved Backflow Prevention Device: Must include isolation valves and test cocks to facilitate in-line testing and repair. The assembly must appear on a current approval list from the American Society of Sanitary Engineering (A.S.S.E.) or on an approval list from the Foundation of Cross-Connection Control and Hydraulic Research at the University of Southern California (FCCC & HR @ USC)

- Reduced Pressure Principle Assembly	A device containing within its structure a minimum of two independently acting approved check valves, together with an automatically operating pressure differential relief valve located between the two check valves. The first check valve reduces the supply pressure a predetermined amount so that during normal flow and at cessation of normal flow the pressure between the checks shall be less than the supply pressure. In case of leakage of either check valve, the differential relief valve, by discharging to the atmosphere, shall operate to maintain the pressure between the checks less than the supply pressure. The unit shall include tightly closing shutoff valves located at each end of the device, and each device shall be fitted with properly located test cocks. The entire assembly shall meet the design and performance specifications and approval of a recognized and City-approved testing agency for backflow prevention assemblies.    To be approved, these assemblies must be readily accessible for in-line maintenance and testing and be installed in a location where no part of the assembly will be submerged.

- Double Check Valve Assembly:	An assembly composed of two single, independently acting, check valves, including tightly closing shutoff valves located at each end of the assembly and suitable connections for testing the water tightness of each check valve, plus properly located test cocks for the testing of each check valve.. A check valve is a valve that is drip-tight in the normal direction of flow when the inlet pressure is one psi and the outlet pressure is zero. The check valve shall permit no leakage in a direction reverse to the normal flow. The closure element (e.g., clapper) shall be internally weighted or otherwise internally loaded to promote rapid and positive closure. The entire assembly shall meet the design and performance specifications and approval of a recognized and City-approved testing agency for backflow prevention assemblies.  To be approved, these assemblies must be readily accessible for in-line maintenance and testing.

- Double Check Valve    A compact unit manufactured with two independent spring actuated check valves. The residential dual check is acceptable for use back-flow prevention in areas served by reuse systems defined in FAC Chapter 62-610, Part III, as defined in paragraphs (5)(a) and (5)(b)

- Atmospheric vacuum breaker  An anti-siphon backflow prevention device that incorporates an air inlet to prevent backflow by backsiphonage.  Designed to protect against high and low hazards during a backsiphonage condition only.  Sometimes includes a shut-off valve on the upstream side only.

- Pressure vacuum breaker  an assembly containing one independently operated internally loaded check valve and an independently operated internally loaded air inlet valve located on the discharge side of the check.  Assembly includes tightly closing shut-off valves on the inlet and outlet sides of the assembly and properly located test cocks

- Spill Resistant Pressure Vacuum Breaker  an assembly designed to prevent backsiphonage that can be used under continuous pressure; the assembly includes an independently operating spring loaded check valve and an independently loaded air inlet valve located on the discharge side of the check with shut-off valves located on the inlet and outlet side of the assembly, a resilient seated test cock located downstream of the number one shut-off valve and upstream of the check valve with a properly located air vent above the check valve and below the air inlet valve

- Hose Bibb Vacuum Breaker: A deice which is permanently attacked to a hose bibb and which acts  as an atmospheric vacuum breaker.

(i)        Contamination:	Means an impairment of the quality of the potable water by sewage, industrial fluids or waste liquids, compounds or other materials to a degree which creates an actual hazard to the public health through poisoning or through the spread of disease.

(j)     Cross-Connection:	Any physical connection or arrangement of piping or fixtures between two otherwise separate piping systems one of which contains potable water and the other non-potable water or industrial fluids of questionable safety, through which, or because of which, backflow by backpressure or  backsiphonage may occur into the potable water system.  A water service connection between a public potable water distribution system and a customer’s water distribution system which is cross-connection to a contaminated fixture, industrial fluid system or with a potentially contaminated supply or auxiliary water system, constitutes one type of cross-connection.  Other types of cross-connections include connectors such as swing connections, removable sections, four-way valves, spools, dummy sections of pipe, swivel or change-over devices, sliding multi-port tube, solid connections, etc.

(k)        Cross-Connections – Controlled:	A connection between a potable water system and a non-potable water system with an approved backflow prevention assembly properly installed that will continuously afford the protection commensurate with the degree of hazard.

(l)    Cross-Connection Control by Containment:	The installation of an approved backflow prevention assembly at the water service connection to any customer’s premises where it is physically and economically infeasible to find and permanently eliminate or control all actual or potential cross-connections within the customer’s water system; or, it shall mean the installation of an approves backflow prevention assembly on the service line leading to and supplying a portion of a customer’s water system where there are actual or potential cross-connections which cannot be effectively eliminated or controlled at the point of cross-connection.

(m)      Director of Utilities:	The Director of Utilities, or his designee in charge of the Water Department with the authority and responsibility for the implementation of an effective cross-connection control program and for the enforcement of the provisions of this Ordinance.

(n)      Hazard, Degree of:	The term is derived from an evaluation of the potential risk to public health and the adverse affect of the hazard upon the potable water system.

- Hazard-Health:	Any condition, device or practice in the water supply system and its operation which could create, or in the judgment of the Director, or his designee may create a danger to the health and well-being of the water consumer.  An example of a health hazard is a structural defect, including cross-connection, in a water supply system.

- Hazard-Plumbing: A plumbing type cross-connection in a consumer’s potable water system or to the potability of the public or the consumer’s potable water system but which would constitute a nuisance or be aesthetically objectionable or could cause damage to the system or its appurtenances, but would not be dangerous to health.

- Hazard-Pollutional:  An actual or potential threat to the physical properties of the water system or to the potability of the public or the consumer’s potable water system but which would constitute a nuisance or be aesthetically objectionable or could cause damage to the system or its appurtenances, but would

(o)    Hazard-System:	An actual or potential threat of severe damage to the physical properties of the public potable water system or the consumer’s potable water system or of a pollution or contamination which would have a protracted effect on the quality of the potable water in the system.

(p)   Industrial Fluids System:	Any system containing a fluid or solution which may be chemically, biologically or otherwise contaminated or polluted in a form or concentration such as would constitute a health, system, pollutional or plumbing hazard is introduced into an approved water supply.  This may include, but not be limited to: polluted or contaminated waters; all types of process waters and “used waters” originating from the public potable water system which may have deteriorated in sanitary quality; chemicals in fluid form; plating acids and alkalies, circulated cooling water connected to an open cooling tower and/or cooling towers that are chemically or biologically treated or stabilized with toxic substances; contaminated natural water such as from wells, springs, streams, rivers, bays, harbors, seas, irrigation canals or systems, etc.; oils, gases, glycerin, paraffin’s, caustic and acid solutions and other liquids and gaseous fluids used in industrial or other purposes or for fire-fighting purposes.

(q)   Isolation: Isolation consists of two types, fixture isolation and area or zone isolation. Isolation at a fixture means installing an approved backflow preventer at the source of the potential contamination. Isolation at an area or zone is confining the potential source of contamination within a specific area. Isolation may be appropriate with or without containment depending on the whether the conditions create a health or non-health hazard.

(r)  Pollution:	Means the presence of any foreign substance (organic, inorganic or biological) in water which tends to degrade its quality so as to constitute a hazard or impair the usefulness or quality of the water to a degree which does not create an actual hazard to the public health but which does adversely and unreasonably affect such waters for domestic use.

(s)    Water-Potable:	Any water, which, according to recognized standards is safe for human consumption.

(t)   Water-Non Potable:	Water which is not safe for human consumption or which is of questionable potability.

(u)    Water Purveyor:	The term water purveyor shall mean the owner or operator of the public potable water system supplying an approved water supply to the public.  As used herein, the terms water purveyor and City of ___________________________________ may be used synonymously.

(v)   Water Service Connections:	The terminal end of a service connection form the public potable water system i.e., where the Water Purveyor loses jurisdiction and sanitary control over the water at its point of delivery to the customer’s water system.  If a meter is installed at the end of the service connection, then the service connection shall mean the downstream and of the meter.  There should be no unprotected takeoffs from the service line ahead of any meter or backflow prevention assembly located at the point of delivery to the customer’s water system.  Service connection shall also include water service connection from a fire hydrant and all other temporary or emergency water service connections form the public water system.

(w) Water-Used:	Any water supplied by a water purveyor from a public potable water system to a consumer’s water system after it has passed through the point of delivery and is no longer under the sanitary control of the Water Purveyor.

SECTION 4.		REQUIREMENTS:

The water system shall be considered as made up of two parts: the utility system and the customer system.

- Utility system shall consist of the source facilities and the distribution

system, and shall include all those facilities of the water system under the complete

control of the utility, up to the point where the customer’s system begins.

- Source shall include all components of the facilities utilized in the

production, treatment, storage, and delivery of water to the distribution system.

- Distribution system shall include the network of conduits used for the

delivery of water from the source to the customer’s system.

- Customer’s system shall include those parts of the facilities beyond the termination of the utility distribution system that are utilized in conveying

utility-delivered domestic water to points of use.

SECTION 5.		POLICY:

a)        No water service connection to any premises shall be installed or maintained by the Water Purveyor unless the water supply is protected as required by State laws and regulations and this Ordinance.  Service of water to any premises shall be discontinued by the Water Purveyor if a backflow prevention assembly required by this Ordinance is not installed, tested and maintained, or if it is found that a backflow prevention. Any water assembly has been removed, by-passed, or if an unprotected cross-connection exists on the premises. Service will not be restored until such conditions or defects are corrected.

b)      The customer’s system should be open for inspection at all reasonable times to authorized representatives of the City of _________________________________ to determine whether cross-connections or other structural or sanitary hazards, including violations of these regulations exist.  Water service may be discontinued after reasonable notice to the Consumer if a violation of this Ordinance exists on the premises, and such other precautionary measures may be taken as are deemed necessary to eliminate any danger to the potable water.  Water service shall not be restored until the danger had been eliminated in compliance with the provisions of this Ordinance.

c)   An approved backflow-prevention assembly shall be installed on each service line to a customer’s water system at or near the property line or immediately inside the building being served; but in all cases, before the first branch line leading off the service line wherever the following conditions exist:

- In the case of premises having an auxiliary water supply which is not or may not be of safe bacteriological or chemical quality and which is not acceptable as an additional source by the Director, or his designee, the public water system shall be protected against backflow from the premises by installing a backflow prevention assembly in the service line appropriate to the degree of hazard.

- In the case of premises on which any industrial fluids or any other objectionable substance is handled in such a fashion as to create an actual or potential hazard to the public water system, the public system shall be protected against backflow from the premises by installing a backflow prevention assembly in the service line appropriate to the degree of hazard.  This shall include the handling of process waters and waters originating from the utility system which have been subject to deterioration in quality.

- In the case of premises having (1) internal cross-connections that cannot be permanently corrected and controlled, or (2) intricate plumbing and piping arrangements or where entry to all portions of the premises is not readily accessible for inspection purposes, making it impracticable or impossible to as certain whether or not dangerous cross-connections exist, the public water system shall be protected against backflow from the premises by installing a backflow prevention device assembly in the service line.

d)     The type of protection assembly required under Section 4.  (c)-(i), (ii), and (iii) shall depend upon the degree of hazard which exists as follows:

  - In the case of any premises where there is an auxiliary water supply as stated in sub-section (c)-(i) of this Section and it is not subject to any of the following rules, the public water system shall be protected by an approved air-gap separation or an approved reduced pressure principle backflow prevention assembly.

  - In the case of any premises where there is water or substance that would be objectionable but not hazardous to health, if introduced into the public water system, the public water system shall be protected by an approved double check valve assembly.

  - In the case of any premises where there is any material dangerous to health which is handled in such a fashion as to create an actual or potential hazard to the public water system, the public water system shall be protected by an approved air gap separation or an approved reduced pressure principle backflow prevention assembly.  Example of premises where these conditions will exist include sewage treatment plants, sewage pumping station, chemical manufacturing plants, hospitals, mortuaries and plating plants.

  - In the case of any problems where there are “un-controlled” cross-connections, either actual or potential, the public water system shall be protected by an approved air-gap separation or an approved reduced pressure principle backflow prevention assembly at the service connection.

  - In case of any premises where, because of security requirements or other prohibitions or restrictions it is impossible or impractical to make a complete in-plant cross-connection survey, the public water system shall be protected against backflow by backpressure or backsiponage from the premises device in the service line.  In this case, maximum protection will be required; that is, an approved air-gap separation or an approved reduced pressure principle backflow prevention assembly shall be installed in each service to the premises.

e)      Any backflow prevention assembly required herein shall be of a model and size approved by the Director of Utilities, or his/her designee.  The term “Approved Backflow Prevention Assembly ” shall mean a device that has been manufactured in full conformance with the standards established by the American Water Works Association entitled: 1.) AWWA C510-97 - Double Check Valve Backflow Prevention Assembly and 2.) AWWA C511-97   Reduced Pressure Principle and Double Check Valve Backflow Prevention Assembly  as well as the standards set forth by the Foundation for Cross-Connection Control and Hydraulic Research of the University of Southern California.It shall be the duty of the customer-user at any premises where backflow prevention assemblies are installed to have certified inspections and operational tests made at lest once per year.  In those instances where the Director of Utilities, or his designee, deems the hazard to be great enough, he may require certified inspections at more frequent intervals.  These inspections and tests shall be performed by the assembly manufacturer’s representative, or by a certified tester approved by the Director of Utilities, or his designee.  It shall be the duty of the Director, or his designee, to see that these timely tests are made.  The customer-user shall notify the Director, or his designee, in advance when the tests are to be undertaken so that he or his representative may witness the tests if it is so desired.  These assemblies shall be repaired, overhauled, or replaced at the expense of the customer-user whenever said assemblies are found to be defective.  Records of such test, repairs, and overhaul shall be kept and copies sent to the Water Distribution Office of the City Clerk.

g)      All presently installed backflow prevention assemblies which do not meet the requirements of this section but were approved assemblies for the purposes described herein at the time of installation and which have been properly maintained, shall, except for the inspection and maintenance requirements under sub-section (f), be excluded from the requirements of these rules so long as the Director of Utilities is assured that they will satisfactorily protect the utility system.  Whenever the existing assembly is moved from the present location or requires more than minimum maintenance or when the Director, or his designee, finds that the maintenance constitutes a hazard to health, the unit shall be replaced by a backflow prevention assembly meeting the requirements of this section.

h)      Nothing herein shall relieve the consumer of the responsibility for conducting, or causing to be conducted, periodic surveys of water use practices on his premises to determine where there are actual or potential cross-connections in the consumer’s water system through which contaminants or pollutants could flow back into a public water system or potable consumer’s water system.

Section 6. 	DESIGNATED FACILTIES

(a)          Facilities that have been identified where backflow preventers as required by the City. They include but are not limited to the following:

Beverage bottling plants,
Car washes,
High-rise buildings,
Canneries, packing houses and reduction plants,
Dairies,
Films and other laboratories,
Commercial laundries and dyeworks (excluding coin laundries),
Wastewater facilities,
Metal manufacturing, cleaning, processing, and fabricating plants,
Oil and gas production, storage and transmission facilities,
Plating plants and facilities,
Radioactive materials, research, production and utilization plants,
Restricted, classified and other facilities closed to inspection,
Steam generating facilities,
Schools and colleges with laboratories,
Sand and gravel plants,
Hospitals, medical buildings, doctors’ offices, veterinarians’ offices, sanitariums, morgues, mortuaries, autopsy facilities, nursing and convalescent homes and clinics,
Meat packing plants or related facilities,
Fire fighting systems, including reservoirs, which are subject to contamination with anti-freeze solutions, “Foamite”, or other chemicals or compounds used in fighting fires,
Auxiliary water systems,
Irrigation systems.

Backflow preventers may be required by the Director of Utilities, or his designee, for other facilities not listed if deemed necessary to protect the water system form possible contamination.

Section 7.	Penalty for Non-Compliance

Water service will be discontinued after reasonable notice to the Customer if a violation of this Ordinance exists on the premises, and such other precautionary measures may be taken as are deemed necessary to eliminate any danger to the potable water.  Water service will be discontinued if the proper backflow prevention assembly is not installed or not tested at least annually or not repaired when the assembly fails to meet minimum design standards.  Water service shall not be restored until the danger had been eliminated in compliance with the provisions of this Ordinance.

Section 8.	Conflicts in Ordinance

All ordinances or parts of ordinances in conflict or inconsistent with the provisions of this Ordinance be, and the same hereby repealed.

Section 9. 	EFFECTIVE DATE

This Ordinance shall take effect from and after its passage, approval, recording, and publication as provided by law.

PASSED AND ADOPTED in open session this __________ day of ________, 20__.

Appendix 8 - 	Cross-Connection Educational Brochure for Homeowners

Cross-Connection Prevention for Homeowners

Contamination of your water can be caused by how you use water in your home. You may be surprised how many different ways that water can become contaminated by inadvertent misused.

This brochure discusses a few of the uses of water that may cause the water that you use   to become contaminated if simple back flow procedures are not followed.

Sinks, Tubs, Tanks

The faucets in your bathroom or kitchen must be located so that the end of the faucet is above the overflow level of the sink or tub.

Fill lines to water troughs or tanks must also be physically separated or “air-gapped.”

If there is no air-gap, then the contents of the sink, tub, or tank may be sucked or “backsiphoned” into the water line during a

loss of water pressure.

Backflow Caused by a Submerged

Drain Hose with no Air Gap.

Never Submerge the end of a hose in a sink or a drain!

Bathroom and Kitchen Plumbing Fixtures

Toilet Showing Water Inlet above

Water Surface

## Toilets

Toilets need water to flush the waste material into the sewer system. The water that flushes the toilet enters into the toilet tank from the small hose or pipe connected to the bottom of the toilet tank. It is essential that the float-valve (or anti-siphon ballcock) inside of the toilet tank is the correct type so that the contents of the toilet tank don’t get back into the drinking water system in your house. As shown in the illustration, the anti-siphon ballcock and refill tube must be above the water level in the tank.

Submerged Drain

From Washing

Machine with no Air Gap

### Washing Machines and Dishwashers

In addition, no appliance drains such as a dishwasher or a dishwasher should never be drained directly to a sanitary drain without an air gap. The air gap prevents any type of siphoning effect.

##### Lawn and Flower Irrigation

Irrigation systems make watering of your lawn or garden much easier, but if not properly

constructed, contaminants may backflow into your drinking water. Backflow from hoses can be prevented by the use of some simple cross-connection control devices.

Water pooling around sprinkler heads may be contaminated by chemicals, fertilizers, or

animal waste. For permanent installations a atmospheric vacuum breaker must be installed to prevent backflow from occurring.

# Hose bibs

Hose bibbs are part of our everyday life. They allow us to hook up a garden hose to water the plants, wash the car, clean out the gutters, fill the swimming pool, etc.

However, every time you connect a garden hose to a hose bibb, you are extending the end of the water line.

To make sure that no harmful materials are drawn back into the garden

hose, a vacuum breaker should be installed on each hose bibb.

___

__

Adapted from

Foundation for Cross-Connection

Control and Hydraulic Research

2002 © University of Southern California

__

__

## Appendix 9 -

#### Standard Piping Color Codes for Water Works Facilities

To facilitate identification of piping in plants and pumping stations it is recommended that the following color scheme be utilized:

| Water Lines |  |
| --- | --- |
| Raw | Olive Green |
| Settled or Clarified | Aqua |
| Finished or Potable | Dark Blue |
| Chemical Lines |  |
| Alum or Primary Coagulant | Orange |
| Ammonia | White |
| Carbon Slurry | Black |
| Caustic | Yellow with Green Band |
| Chlorine (Gas and Solution) | Yellow |
| Chlorine Dioxide | Yellow with Violet Band |
| Fluoride | Light Blue with Red Band |
| Lime Slurry | Light Green |
| Ozone | Yellow with Orange Band |
| Phosphate Compounds | Light Green with Red Band |
| Polymers or Coagulant Aids | Orange with Green Band |
| Potassium Permanganate | Violet |
| Soda Ash | Light Green with Orange Band |
| Sulfuric Acid | Yellow with Red Band |
| Sulfur Dioxide | Light Green with Yellow Band |
| Waste Lines |  |
| Backwash Waste | Light Brown |
| Sludge | Dark Brown |
| Sewer (Sanitary or Other) | Dark Gray |
| Other |  |
| Reclaimed Water | Purple Recommended Standards for Water Works 2003 Edition Health Research Incorporated |
| Gas | Red |
| Other Lines | Light Gray |