## Cover
Water Audit Worksheet
| 8.02% | Estimated Water Loss
FRWA Member: |  |  | City of Normal
Address: |  |  | 100 Oak Avenue
Normal FL 3333
Telephone: |  |  | 850-555-1111
Fax: |  |  | 850-555-1112
Contact: |  |  | Robert Normal, City Administrator
E-mail: |  |  | rnormal@cityofnormal.org
Population: |  |  | 5500
Connections: |  |  | 2000
PWS: |  |  | 1234567
County: |  |  | County
Date: |  | 2007-11-30
|  | Prepared by: | FRWA Circuit Rider
Florida Rural Water Association
2970 Wellington Circle West, Suite 101
Tallahassee, Florida 32309-6885
|  | Phone: | 850-668-2746
|  | Fax: | 850-893-4581

## Audit Sheet
Florida Rural Water Association
|  | Member: | City of Normal | Date: | 2007-11-30
|  | Contact: | Robert Normal, City Administrator | Conn: | 2000
|  | City: | Normal FL 3333 | PWS: | 1234567
|  | By: | FRWA Circuit Rider | County: | County
WATER SYSTEM REVIEW WORKSHEET
Water Volume (MGD)
Line | Item & Description |  |  | SubTotal | Total Cumulative
1 | Uncorrected Total Water Supply to the Distribution System:
| a. | Total from Plant Master Meters: |  | 16629715
| b. | Total Purchased Water: |  | 0
| c. | Total Water Supplied (add 1a+1b): |  |  | 16629715
2 | Adjustments to Total Water Supply:
| a. | Source Meter Error (+ or -): |  | 0
| b. | Change in Reservoir and Tank Storage: |  | 0
| c. | Other Contribution or Losses (+ or -): |  | 0
| d. | Total Adjustments (add 2a+2b+2c): |  | 0 | 0
3 | ADJUSTED TOTAL Water Supply (add 1c+2d): |  |  |  | 16629715
4 | Uncorrected Total Metered Water Use/Sales:
| a. | Total Residential Metered Water Use: |  | 11774000
| b. | Total Commercial Metered Water Use: |  | 0
| c. | Total Institutional Metered Water Use: |  | 0
| d. | Total Other (wholesale) Metered Water Use: |  | 0
| e. | Total Metered Water Use (add 4a+4b+4c+4d): |  |  | 11774000
5 | Adjustments to Total Metered Water Use:
| a. | Adjustments Due to Meter Reading lag (+): |  | 0
| b. | Total Sales Meter & System Meter Errors (+): |  | 0
| c. | Total Adjusted Metered Water Use (add 5a+5b): |  |  | 0
6 | CORRECTED TOTAL Metered Water Use (add 4e+5c): |  |  |  | 11774000
7 | CORRECTED TOTAL UNACCOUNTED-FOR WATER (Subtract line 6 from line 3): |  |  |  | 4855715
8 | Authorized unmetered water uses:
| a. | Firefighting & Training: |  | 0
| b. | Main Flushings: |  | 270000
| c. | Storm Drain Flushing: |  | 0
| d. | Sewer Cleaning |  | 0
| e. | Street Cleanings: |  | 0
| f. | Water Company Use (domestic): |  | 0
| g. | Bulk Water Sales: |  | 0
| h. | Tank Drainings: |  | 12000
| i. | Schools: |  | 0
| j. | Landscaping In Large Public Areas |  | 0
|  | 1. Parks: |  | 0
|  | 2. Golf Courses: |  | 0
|  | 3. Cemeteries: |  | 0
|  | 4. Playgrounds: |  | 0
|  | 5. Highway Median Strips:: |  | 0
|  | 6. Other Landscaping: |  | 0
| k. | Decorative Water Facilities: |  | 0
| l. | Swimming Pools: |  | 0
| m. | Construction Sites: |  | 0
| n. | Water Quality & Other Testing: |  | 0
| o. | Plant Uses: |  | 0
| 1. Chemical Mix & Application: | 1. Chemical Mix & Application: |  | 0
| 2. Filter Wash Water: | 2. Filter Wash Water: |  | 0
| 3. Filter Surface Wash: | 3. Filter Surface Wash: |  | 0
| 4. Pump Priming: | 4. Pump Priming: |  | 0
| 5. Pump Bearing Lubrication: | 5. Pump Bearing Lubrication: |  | 0
| 6. Laboratory Use: | 6. Laboratory Use: |  | 0
| 7. Other Misc. Plant Use: | 7. Other Misc. Plant Use: |  | 0
| p. | Other Unmetered Leaks: |  | 0
| q. | Repaired System Leaks: |  | 3240000
9 | TOTAL Authorized Unmetered Water (add lines 8a through 8q) |  |  |  | 3522000
10 | TOTAL Unaccounted-for Water (subtract line 9 from line 7): |  |  |  | 1333715
11 | IDENTIFIED WATER LOSSES
| a. | Accounting Procedure Errors: |  | 0
| b. | Illegal Connections: |  | 0
| c. | Malfunctioning Distribution System Controls: |  | 0
| d. | Reservoir Seepage & Leakage: |  | 0
| e. | Evaporation: |  | 0
| f. | Reservoir Overflow: |  | 0
| g. | Identified Leakage: |  | 0
| h. | Bleeders & Blow-offs: |  | 0
| i. | Emergency Meter Removal: |  | 0
| j. | Thefts: |  | 0
12 | TOTAL Identified Water Losses (add lines 11a through 11j): |  |  |  | 0
13 | Potential Water System Leakage (subtract line 12 from line 10): |  |  |  | 1333715
|  |  |  | Estimated Percentage Water Loss: | 8.02%
14 | Recoverable Leakage (multiply line 13 by 0.75) |  |  |  | 1000286.25
R
U
R
A
L
R
T
W
A
E
R
O
L
A
D
I
F
A
I
S
O
A
S
C
T
I
O
N
FRWA

## Water Pumped & Sold
Florida Rural Water Association
| Member: | City of Normal |  | Date: | 2007-11-30
| Contact: | Robert Normal, City Administrator |  | Conn: | 2000
| City: | Normal FL 3333 |  | PWS: | 1234567
| By: | FRWA Circuit Rider |  | County: | County
WATER PUMPED, PURCHASED & SOLD ~ AUDIT WORKSHEET
Water Produced (MGD) | 2006-10-01 | 2006-11-01 | 2006-12-01 | 2006-01-01 | 2006-02-01 | 2006-03-05 | 2006-04-01 | 2006-05-01 | 2006-06-01 | 2006-07-01 | 2006-08-01 | 2006-09-01 | Total | Meter % Correction | Corrected Total
Water Plant #1 | 1518000 | 1369947 | 1324451 | 1237800 | 1206800 | 1475950 | 1592808 | 1832448 | 1367782 | 1168366 | 1453850 | 1081513 | 16629715 | 0 | 16629715
Water Plant #2 | [12 empty] | 0 | 0 | 0
Water Plant #3 | [12 empty] | 0 | 0 | 0
Purchased Water | [12 empty] | 0 | 0 | 0
[13 empty] | 0 | 0 | 0
Total | 1518000 | 1369947 | 1324451 | 1237800 | 1206800 | 1475950 | 1592808 | 1832448 | 1367782 | 1168366 | 1453850 | 1081513 | 16629715 | 0 | 16629715
Water Sold (MGD) | 2006-10-01 | 2006-11-01 | 2006-12-01 | 2006-01-01 | 2006-02-01 | 2006-03-05 | 2006-04-01 | 2006-05-01 | 2006-06-01 | 2006-07-01 | 2006-08-01 | 2006-09-01 | Total | Meter % Correction | Corrected Total
Residential | 882000 | 1014000 | 755000 | 779000 | 847000 | 838000 | 1155000 | 1072000 | 973000 | 875000 | 1252000 | 1332000 | 11774000 | 0 | 11774000
Commercial #1 | [12 empty] | 0 | 0 | 0
Institutional | [12 empty] | 0 | 0 | 0
Wholesale Accounts | [12 empty] | 0 | 0 | 0
[13 empty] | 0 | 0 | 0
Total | 882000 | 1014000 | 755000 | 779000 | 847000 | 838000 | 1155000 | 1072000 | 973000 | 875000 | 1252000 | 1332000 | 11774000 | 0 | 11774000
Percent Losses | 41.9% | 25.98% | 43% | 37.07% | 29.81% | 43.22% | 27.49% | 41.5% | 28.86% | 25.11% | 13.88% | -23.16% | 29.2% |  | 29.2%
R
U
R
A
L
R
T
W
A
E
R
O
L
A
D
I
F
A
I
S
O
A
S
C
T
I
O
N
FRWA

## Water Losses
Florida Rural Water Association
| Member: | City of Normal |  | Date: | 2007-11-30
| Contact: | Robert Normal, City Administrator |  | Conn: | 2000
| City: | Normal FL 3333 |  | PWS: | 1234567
| By: | FRWA Circuit Rider |  | County: | County
WATER LOSSES ~ AUDIT WORKSHEET
Authorized Unmetered Water Losses | 2006-10-01 | 2006-11-01 | 2006-12-01 | 2006-01-01 | 2006-02-01 | 2006-03-05 | 2006-04-01 | 2006-05-01 | 2006-06-01 | 2006-07-01 | 2006-08-01 | 2006-09-01 | Total
a. Firefighting & Training | [12 empty] | 0
b. Main Flushings | 22500 | 22500 | 22500 | 22500 | 22500 | 22500 | 22500 | 22500 | 22500 | 22500 | 22500 | 22500 | 270000
c. Storm Drain Flushing | [12 empty] | 0
d. Sewer Cleaning | [12 empty] | 0
e. Street Cleanings | [12 empty] | 0
f. Water Company Use (domestic) | [12 empty] | 0
g. Bulk Water Sales | [12 empty] | 0
h. Tank Drainings |  |  |  |  | 6000 | 6000 | [6 empty] | 12000
i. Schools | [12 empty] | 0
j. Landscaping In Large Public Areas | [12 empty] | 0
1. Parks | [12 empty] | 0
2. Golf Courses | [12 empty] | 0
3. Cemeteries | [12 empty] | 0
4. Playgrounds | [12 empty] | 0
5. Highway Median Strips | [12 empty] | 0
6. Other Landscaping | [12 empty] | 0
k. Decorative Water Facilities | [12 empty] | 0
l .Swimming Pools | [12 empty] | 0
m. Construction Sites | [12 empty] | 0
n. Water Quality & Other Testing | [12 empty] | 0
o. Plant Uses | [12 empty] | 0
1. Chemical Mix & Application | [12 empty] | 0
2. Filter Wash Water | [12 empty] | 0
3. Filter Surface Wash | [12 empty] | 0
4. Pump Priming | [12 empty] | 0
5. Pump Bearing Lubrication | [12 empty] | 0
6. Laboratory Use | [12 empty] | 0
7. Other Misc. Plant Use | [12 empty] | 0
p. Other Unmetered Leaks | [12 empty] | 0
q. Repaired System Leaks | 3240000 | [11 empty] | 3240000
Total | 3262500 | 22500 | 22500 | 22500 | 28500 | 28500 | 22500 | 22500 | 22500 | 22500 | 22500 | 22500 | 3522000
IDENTIFIED Water Losses | 2006-10-01 | 2006-11-01 | 2006-12-01 | 2006-01-01 | 2006-02-01 | 2006-03-05 | 2006-04-01 | 2006-05-01 | 2006-06-01 | 2006-07-01 | 2006-08-01 | 2006-09-01 | Total
a. Accounting Procedure Errors | [12 empty] | 0
b. Illegal Connections | [12 empty] | 0
c. Malfunctioning Distribution System Controls | [12 empty] | 0
d. Reservoir Seepage & Leakage | [12 empty] | 0
e. Evaporation | [12 empty] | 0
f. Reservoir Overflow | [12 empty] | 0
g. Identified Leakage | [12 empty] | 0
h. Bleeders & Blow-offs | [12 empty] | 0
i. Emergency Meter Removal | [12 empty] | 0
j. Thefts | [12 empty] | 0
Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
R
U
R
A
L
R
T
W
A
E
R
O
L
A
D
I
F
A
I
S
O
A
S
C
T
I
O
N
FRWA